## Power Supplies
M4 (Mu2e Section) BEAM LINE POWER SUPPLY REQUIREMENTS
2015-09-11 |  |  | Ramp Cycle Time: | 0.003 |  |  |  | Cabling Assumptions: | [17 empty] | Power Supply Assumptions:
[9 empty] | M&S |  |  | Install | [15 empty] | Power Supply Loses = | 10% | of Load losses
[8 empty] | 500 kcmil: | 5.64 | per ft. |  | 3.61 | per ft | [14 empty] | Power Supply PF = | 0.9 | for SM PSs
[8 empty] | 100 kcmil: | 1.2 | per ft. |  | 1.12 | per ft | [14 empty] | Power Supply PF = | (Voperating/Vmax) for SCR PSs
| Magnet Type | Inductance | Resistance | [6 empty] | Cabling in Service Building: | 30 | ft | [15 empty] | Cost/watt for SM Power Supply = | 0.58 | $/watt
| SQA | 0.04302 | 0.032338 | [6 empty] | MC-1 Building to enclosure cable tray: | 50 | ft | [15 empty] | Cost/watt for SCR Power Supply = | 0.64 | $/watt
| SQB | 0.060228 | 0.039252 | [6 empty] | M4 enclosure begins at 88' along beamline | 88 | ft
| SQC | 0.065964 | 0.041556 | [6 empty] | AP30 M4 Mu2e quad circuits to M4 enclosure | 230 | ft
| SQD | 0.077914 | 0.046357 | [6 empty] | AP30 M4 Mu2e dipole circuits to M4 enclosure | 130 | ft
| SQE | 0.12342 | 0.064639 | [6 empty] | Mu2e Building to tunnel | 50 | ft
| LQC | 0.0304 | 0.0081833 | [6 empty] | Detector Hall Duct Location: | 700 | ft
| LQD | 0.0344 | 0.0087892 | [6 empty] | MC-1 Building Duct Location | 480 | ft
[10 empty] | Tray to load | 10 | ft
NAME | MAGNET LOAD | [6 empty] | LOAD CABLING | [8 empty] | LOAD CHARACTERISTICS | [7 empty] | POWER SUPPLY | [16 empty] | FEEDERS |  |  |  |  | CABLE COUNTS |  | CABLE COUNTS BY BUILDING
P.S. CIRCUIT | MAGNET | M4 - Mu2e Beamline | MAGNET | # | MAG. | MAG. |  | Cable Type | # of cables | R/kFt | L 1-way | Cable RES. | Cable Costs |  |  |  | Total Circuit Res. | Peak Current | Min. Current | dI/dT | Peak VOLT. | RMS CURR. | Peak Power |  | PS Location | PS TYPE | Max. Volt | Max. Curr. | PS Rating | Losses |  | Power Supply Costs |  |  |  | PS Installation Costs | [5 empty] | AVE PWR | kVA | Amps |  |  | Total 500 Cables | Total 100 Cables | AP30 500 Cables | AP30 100 Cables | MC-1 500 Cables | MC-1 100 Cables | Det Hall 500 Cables | Det Hall 100 Cables
NAME | TYPE | Magnet(s) Name(s) & Distance along beamline (ft) | MODEL | MAGs | IND. | RES. |  | kcmil |  | ohms | (ft) | ohms | M&S ($k) | Install ($k) | Tot. Cir ($k) |  | ohms | (amps) | (amps) | (A/s) | (volts) | (amps) | (kW) |  |  | SM or SCR | (volts) | (amps) | (kW) | (kW) |  | M&S ($k) | Tech. Labor (hrs) | Eng. Labor (hrs) |  | M&S ($k) | Tech. Labor (hrs) | Eng. Labor (hrs) | Elect. Labor (hrs) |  |  | (kW) | kVA | I | %V | %I |  |  | 22 | 0 | 36 | 4 | 58 | 0
D:Q908 | Quad. | Q908 116' | SQA | 1 | 0.04302 | 0.032338 |  | 500 | 1 | 0.026 | 268 | 0.013936 | 3.023 | 1.935 | 4.958 |  | 0.046274 | 273.6 | 273.6 | 0 | 12.6607 | 273.6 | 3.464 |  | AP30 | SM | 40 | 375 | 15 | 1.0944 |  | 15.65 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 4.5584 | 5.0649 | 6.0993 | 31.6518 | 72.96 | 2 | 0
D:Q909 | Quad. | Q909 124' | SQA | 1 | 0.04302 | 0.032338 |  | 500 | 1 | 0.026 | 276 | 0.014352 | 3.1133 | 1.9927 | 5.106 |  | 0.04669 | 213.7 | 213.7 | 0 | 9.9778 | 213.7 | 2.1322 |  | AP30 | SM | 32 | 300 | 9.6 | 0.68384 |  | 12.518 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 2.8161 | 3.129 | 3.768 | 31.1805 | 71.2333 | 2 | 0
D:Q910 | Quad. | Q910 136' | SQC | 1 | 0.06596 | 0.041556 |  | 500 | 1 | 0.026 | 288 | 0.014976 | 3.2486 | 2.0794 | 5.328 |  | 0.056532 | 210.7 | 210.7 | 0 | 11.9113 | 210.7 | 2.5097 |  | AP30 | SM | 32 | 300 | 9.6 | 0.67424 |  | 12.518 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 3.184 | 3.5377 | 4.2603 | 37.2229 | 70.2333 | 2 | 0
D:H910 | Dipole | H910 150', H911 166', H912 182', H916 218', H917 232', H918 249' | SDFW-SDF | 6 | 0.05674 | 0.04549 |  | 500 | 3 | 0.026 | 331 | 0.0057373 | 11.201 | 7.1695 | 18.3705 |  | 0.27868 | 805 | 805 | 0 | 224.3353 | 805 | 180.5899 |  | AP30 | SCR | 400 | 1200 | 480 | 32.2 |  | 31 | 28 | 12 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 212.7899 | 379.4141 | 456.9052 | 56.0838 | 67.0833 | 6 | 0 | Use 500 kW PEI supply from AP2 beamline (circuit IB2-7) in F27
D:Q911 | Quad. | Q911 155', Q918 237' | SQC | 2 | 0.06596 | 0.041556 |  | 500 | 1 | 0.026 | 389 | 0.020228 | 4.3879 | 2.8086 | 7.1965 |  | 0.10334 | 202.6 | 202.6 | 0 | 20.9367 | 202.6 | 4.2418 |  | AP30 | SM | 32 | 300 | 9.6 | 0.64832 |  | 12.518 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 4.8901 | 5.4334 | 6.5432 | 65.4273 | 67.5333 | 2 | 0
D:Q912 | Quad. | Q912 170', Q917 221' | SQA | 2 | 0.04302 | 0.032338 |  | 500 | 1 | 0.026 | 373 | 0.019396 | 4.2074 | 2.6931 | 6.9005 |  | 0.084073 | 186.7 | 186.7 | 0 | 15.6964 | 186.7 | 2.9305 |  | AP30 | SM | 20 | 250 | 5 | 0.3734 |  | 9.85 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 3.3039 | 3.671 | 4.4208 | 78.4821 | 74.68 | 2 | 0
D:Q913 | Quad. | Q913 187', Q916 206' | SQD | 2 | 0.077914 | 0.046357 |  | 500 | 2 | 0.026 | 358 | 0.009308 | 8.0765 | 5.1695 | 13.246 |  | 0.10202 | 321.1 | 321.1 | 0 | 32.7592 | 321.1 | 10.519 |  | AP30 | SM | 50 | 400 | 20 | 1.6055 |  | 18.55 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 12.1245 | 13.4716 | 16.2231 | 65.5184 | 80.275 | 4 | 0
D:Q914 | Quad. | Q914 190', Q915 202' | SQD | 2 | 0.077914 | 0.046357 |  | 500 | 1 | 0.026 | 354 | 0.018408 | 3.9931 | 2.5559 | 6.549 |  | 0.11112 | 287.2 | 287.2 | 0 | 31.9142 | 287.2 | 9.1658 |  | AP30 | SM | 40 | 375 | 15 | 1.1488 |  | 15.65 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 10.3146 | 11.4606 | 13.8013 | 79.7855 | 76.5867 | 2 | 0
7 Circuits | [41 empty] | 253.9813 | 425.1824 | 512.0212 |  |  | 22 | 0 |  | AP30 Fdr Pwr: | 253.9813 | kW
D:Q919 | Quad. | Q919 256' thru Q923 325' | SQA | 5 | 0.04302 | 0.032338 |  | 500 | 1 | 0.026 | 314 | 0.016328 | 3.5419 | 2.2671 | 5.809 |  | 0.17802 | 187 | 187 | 0 | 33.2898 | 187 | 6.2252 |  | MC-1 | SM | 50 | 400 | 20 | 0.935 |  | 18.55 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 7.1602 | 7.9558 | 9.5807 | 66.5797 | 46.75 | 2 | 0 |  | AP30 Fdr V-A: | 425.1824 | kVA
D:Q924 | Quad. | Q924 345' | SQA | 1 | 0.04302 | 0.032338 |  | 500 | 1 | 0.026 | 225 | 0.0117 | 2.538 | 1.6245 | 4.1625 |  | 0.044038 | 173.8 | 173.8 | 0 | 7.6539 | 173.8 | 1.3302 |  | MC-1 | SM | 20 | 250 | 5 | 0.3476 |  | 9.85 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 1.6778 | 1.8643 | 2.245 | 38.2695 | 69.52 | 2 | 0
D:Q925 | Quad. | Q925 362' | SQA | 1 | 0.04302 | 0.032338 |  | 500 | 1 | 0.026 | 208 | 0.010816 | 2.3462 | 1.5018 | 3.848 |  | 0.043154 | 115.3 | 115.3 | 0 | 4.9757 | 115.3 | 0.5737 |  | MC-1 | SM | 20 | 250 | 5 | 0.2306 |  | 9.85 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 0.8043 | 0.89367 | 1.0762 | 24.8786 | 46.12 | 2 | 0
D:Q926 | Quad. | Q926 365' | SQA | 1 | 0.04302 | 0.032338 |  | 500 | 1 | 0.026 | 205 | 0.01066 | 2.3124 | 1.4801 | 3.7925 |  | 0.042998 | 107.8 | 107.8 | 0 | 4.6352 | 107.8 | 0.49968 |  | MC-1 | SM | 20 | 250 | 5 | 0.2156 |  | 9.85 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 0.71528 | 0.79475 | 0.95707 | 23.1762 | 43.12 | 2 | 0
D:Q927 | Quad. | Q927 387' | SQA | 1 | 0.04302 | 0.032338 |  | 500 | 1 | 0.026 | 183 | 0.009516 | 2.0642 | 1.3213 | 3.3855 |  | 0.041855 | 107.8 | 107.8 | 0 | 4.5119 | 107.8 | 0.48638 |  | MC-1 | SM | 20 | 250 | 5 | 0.2156 |  | 9.85 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 0.70198 | 0.77998 | 0.93929 | 22.5596 | 43.12 | 2 | 0
D:Q928 | Quad. | Q928 416' | SQB | 1 | 0.060228 | 0.039252 |  | 500 | 1 | 0.026 | 154 | 0.008008 | 1.7371 | 1.1119 | 2.849 |  | 0.04726 | 203.5 | 203.5 | 0 | 9.6173 | 203.5 | 1.9571 |  | MC-1 | SM | 32 | 300 | 9.6 | 0.6512 |  | 12.518 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 2.6083 | 2.8981 | 3.4901 | 30.0542 | 67.8333 | 2 | 0
D:Q929 | Quad. | Q929 436' | SQA | 1 | 0.04302 | 0.032338 |  | 500 | 1 | 0.026 | 134 | 0.006968 | 1.5115 | 0.96748 | 2.479 |  | 0.039307 | 142.5 | 142.5 | 0 | 5.6012 | 142.5 | 0.79817 |  | MC-1 | SM | 20 | 250 | 5 | 0.285 |  | 9.85 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 1.0832 | 1.2035 | 1.4493 | 28.0059 | 57 | 2 | 0
ACDipole
ACDipole
D:Q930 | Quad. | Q930 463" | SQA | 1 | 0.04302 | 0.032338 |  | 500 | 1 | 0.026 | 107 | 0.005564 | 1.207 | 0.77254 | 1.9795 |  | 0.037902 | 154.9 | 154.9 | 0 | 5.8711 | 154.9 | 0.90943 |  | MC-1 | SM | 20 | 250 | 5 | 0.3098 |  | 9.85 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 1.2192 | 1.3547 | 1.6314 | 29.3555 | 61.96 | 2 | 0
D:Q931 | Quad. | Q931 480" | SQA | 1 | 0.04302 | 0.032338 |  | 500 | 1 | 0.026 | 90 | 0.00468 | 1.0152 | 0.6498 | 1.665 |  | 0.037018 | 188.7 | 188.7 | 0 | 6.9854 | 188.7 | 1.3181 |  | MC-1 | SM | 20 | 250 | 5 | 0.3774 |  | 9.85 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 1.6955 | 1.8839 | 2.2687 | 34.927 | 75.48 | 2 | 0
D:Q932 | Quad. | Q932 533" | SQA | 1 | 0.04302 | 0.032338 |  | 500 | 1 | 0.026 | 143 | 0.007436 | 1.613 | 1.0325 | 2.6455 |  | 0.039774 | 109.8 | 109.8 | 0 | 4.3672 | 109.8 | 0.47952 |  | MC-1 | SM | 20 | 250 | 5 | 0.2196 |  | 9.85 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 0.69912 | 0.7768 | 0.93546 | 21.8362 | 43.92 | 2 | 0
D:Q933 | Quad. | Q933 556" | SQB | 1 | 0.060228 | 0.039252 |  | 500 | 1 | 0.026 | 166 | 0.008632 | 1.8725 | 1.1985 | 3.071 |  | 0.047884 | 253.8 | 253.8 | 0 | 12.1529 | 253.8 | 3.0844 |  | MC-1 | SM | 50 | 400 | 20 | 1.269 |  | 18.55 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 4.3534 | 4.8371 | 5.825 | 24.3058 | 63.45 | 2 | 0
D:HDA1 | Dipole | HDA1 571' Absorber 5 degree dipole magnet | MDCE | 1 | 0.01067 | 0.049 |  | 500 | 4 | 0.026 | 191 | 0.002483 | 8.6179 | 5.5161 | 14.134 |  | 0.051483 | 1165 | 1165 | 0 | 59.9777 | 1165 | 69.874 |  | MC-1 | SCR | 200 | 1200 | 240 | 23.3 |  | 16 | 28 | 12 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 93.174 | 310.6955 | 374.1517 | 29.9888 | 97.0833 | 8 | 0 | Surplus 240kW PEI power supply
D:QDA01 | Quad. | QDA01 600' Absorber quadrupole 1 | 3Q120 | 1 | 0.12342 | 0.169 |  | 100 | 1 | 0.122 | 210 | 0.05124 | 0.504 | 0.4704 | 0.9744 |  | 0.22024 | 80 | 80 | 0 | 17.6192 | 80 | 1.4095 |  | MC-1 | SM | 20 | 250 | 5 | 0.16 |  | 9.85 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 1.5695 | 1.7439 | 2.1001 | 88.096 | 32 | 0 | 2
D:QDA02 | Quad. | QDA02 600' Absorber quadrupole 2 | 3Q120 | 1 | 0.12342 | 0.169 |  | 100 | 1 | 0.122 | 210 | 0.05124 | 0.504 | 0.4704 | 0.9744 |  | 0.22024 | 80 | 80 | 0 | 17.6192 | 80 | 1.4095 |  | MC-1 | SM | 20 | 250 | 5 | 0.16 |  | 9.85 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 1.5695 | 1.7439 | 2.1001 | 88.096 | 32 | 0 | 2
D:Q934 | Quad. | Q934 592' | SQB | 1 | 0.060228 | 0.039252 |  | 500 | 1 | 0.026 | 202 | 0.010504 | 2.2786 | 1.4584 | 3.737 |  | 0.049756 | 192.2 | 192.2 | 0 | 9.563 | 192.2 | 1.838 |  | MC-1 | SM | 20 | 250 | 5 | 0.3844 |  | 9.85 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 2.2224 | 2.4694 | 2.9737 | 47.8152 | 76.88 | 2 | 0
D:Q935 | Quad. | Q935 609' | SQE | 1 | 0.04302 | 0.064639 |  | 500 | 1 | 0.026 | 219 | 0.011388 | 2.4703 | 1.5812 | 4.0515 |  | 0.076026 | 201.6 | 201.6 | 0 | 15.3269 | 201.6 | 3.0899 |  | MC-1 | SM | 32 | 300 | 9.6 | 0.64512 |  | 12.518 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 3.735 | 4.15 | 4.9976 | 47.8967 | 67.2 | 2 | 0
D:Q936 | Quad. | Q936 617' | SQB | 1 | 0.060228 | 0.039252 |  | 500 | 1 | 0.026 | 227 | 0.011804 | 2.5606 | 1.6389 | 4.1995 |  | 0.051056 | 273.5 | 273.5 | 0 | 13.9637 | 273.5 | 3.8191 |  | MC-1 | SM | 50 | 400 | 20 | 1.3675 |  | 18.55 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 5.1866 | 5.7629 | 6.9399 | 27.9275 | 68.375 | 2 | 0
17 Circuits | [41 empty] | 130.1755 | 351.8083 | 423.6613 |  |  | 36 | 4 |  | MC-1 Fdr Pwr: | 130.1755 | kW
| Shield Wall | [48 empty] | MC-1 Fdr V-A: | 351.8083 | kVA
D:V936 | Dipole | V936 672' | CDA | 1 | 0.0107 | 0.027 |  | 500 | 4 | 0.026 | 118 | 0.001534 | 5.3242 | 3.4078 | 8.732 |  | 0.028534 | 970 | 970 | 0 | 27.678 | 970 | 26.8476 |  | Mu2e Bld. | SM | 32 | 1350 | 43.2 | 3.104 |  | 32.006 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 29.9516 | 33.2796 | 40.0766 | 86.4937 | 71.8519 | 8 | 0
D:Q937 | Quad. | Q937 675', Q943 770' | LQC | 2 | 0.0304 | 0.0081833 |  | 500 | 3 | 0.026 | 185 | 0.0032067 | 6.2604 | 4.0071 | 10.2675 |  | 0.019573 | 787.8 | 787.8 | 0 | 15.4198 | 787.8 | 12.1477 |  | Mu2e Bld. | SM | 32 | 1350 | 43.2 | 2.521 |  | 32.006 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 14.6687 | 16.2985 | 19.6273 | 48.1869 | 58.3556 | 6 | 0
D:Q938 | Quad. | Q938 686', Q942 760' | LQD | 2 | 0.0344 | 0.0087892 |  | 500 | 5 | 0.026 | 164 | 0.0017056 | 9.2496 | 5.9204 | 15.17 |  | 0.019284 | 1364.1 | 1364.1 | 0 | 26.3053 | 1364.1 | 35.8831 |  | Mu2e Bld. | SCR | 37.5 | 2000 | 75 | 5.1154 |  | 53 | 28 | 12 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 40.9984 | 58.4461 | 70.383 | 70.1475 | 68.205 | 10 | 0 | New 75kW Spang power supply
D:Q939 | Quad. | Q939 702', Q941 743' | LQC | 2 | 0.0304 | 0.0081833 |  | 500 | 3 | 0.026 | 133 | 0.0023053 | 4.5007 | 2.8808 | 7.3815 |  | 0.018672 | 814.2 | 814.2 | 0 | 15.2027 | 814.2 | 12.378 |  | Mu2e Bld. | SM | 32 | 1350 | 43.2 | 2.6054 |  | 32.006 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 14.9835 | 16.6483 | 20.0485 | 47.5084 | 60.3111 | 6 | 0
D:Q940 | Quad. | Q940 722' | SQA | 1 | 0.04302 | 0.032338 |  | 500 | 1 | 0.026 | 112 | 0.005824 | 1.2634 | 0.80864 | 2.072 |  | 0.038163 | 208.6 | 208.6 | 0 | 7.9607 | 208.6 | 1.6606 |  | Mu2e Bld. | SM | 32 | 300 | 9.6 | 0.66752 |  | 12.518 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 2.3281 | 2.5868 | 3.1151 | 24.8772 | 69.5333 | 2 | 0
D:HT940 | Dipole | HT940 729' | CDA | 1 | 0.0107 | 0.027 |  | 500 | 2 | 0.026 | 119 | 0.003094 | 2.6846 | 1.7184 | 4.403 |  | 0.030094 | 303.1 | 303.1 | 0 | 9.1215 | 303.1 | 2.7647 |  | Mu2e Bld. | SM | 20 | 500 | 10 | 0.6062 |  | 12.75 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 3.3709 | 3.7455 | 4.5104 | 45.6075 | 60.62 | 4 | 0
D:VT940 | Dipole | VT940 735' | CDA | 1 | 0.0107 | 0.027 |  | 500 | 2 | 0.026 | 125 | 0.00325 | 2.82 | 1.805 | 4.625 |  | 0.03025 | 545.6 | 545.6 | 0 | 16.5044 | 545.6 | 9.0048 |  | Mu2e Bld. | SM | 32 | 1350 | 43.2 | 1.7459 |  | 32.006 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 10.7507 | 11.9452 | 14.3849 | 51.5763 | 40.4148 | 4 | 0
D:VT942 | Dipole | VT942 766' | CDA | 1 | 0.0107 | 0.027 |  | 500 | 3 | 0.026 | 156 | 0.002704 | 5.279 | 3.379 | 8.658 |  | 0.029704 | 852.8 | 852.8 | 0 | 25.3316 | 852.8 | 21.6028 |  | Mu2e Bld. | SM | 32 | 1350 | 43.2 | 2.729 |  | 32.006 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 24.3317 | 27.0352 | 32.5569 | 79.1612 | 63.1704 | 6 | 0
D:V943 | Dipole | V943 776' | CDA | 1 | 0.0107 | 0.027 |  | 500 | 4 | 0.026 | 166 | 0.002158 | 7.4899 | 4.7941 | 12.284 |  | 0.029158 | 970 | 970 | 0 | 28.2833 | 970 | 27.4348 |  | Mu2e Bld. | SM | 32 | 1350 | 43.2 | 3.104 |  | 32.006 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 30.5388 | 33.932 | 40.8622 | 88.3852 | 71.8519 | 8 | 0
D:HT943 | Dipole | HT943 782' | CDA | 1 | 0.0107 | 0.027 |  | 500 | 2 | 0.026 | 172 | 0.004472 | 3.8803 | 2.4837 | 6.364 |  | 0.031472 | 586 | 586 | 0 | 18.4426 | 586 | 10.8074 |  | Mu2e Bld. | SM | 32 | 1350 | 43.2 | 1.8752 |  | 32.006 | 148 | 28 |  | 1.5 | 8 | 8 | 17.1429 |  |  | 12.6826 | 14.0917 | 16.9698 | 57.6331 | 43.4074 | 4 | 0 |  | Mu2e Fdr Pwr: | 184.6051 | kW
10 Circuits | [12 empty] | 128.6976 | 82.6712 | [27 empty] | 184.6051 | 218.009 | 262.5349 |  |  | 58 | 0 |  | Mu2e Fdr Pwr: | 218.009 | kVA
[14 empty] | TOTAL CABLE COSTS ($k): | 211.3688 | [6 empty] | Total Peak Power: | 475.1864 | kW | [6 empty] | TOTAL PS COSTS, M&S ($k): | 635.6
[33 empty] | Tech | Eng
[32 empty] | Total PS Labor (hrs): | 4820 | 932
[32 empty] | (man-months): | 30.125 | 5.825
[35 empty] | Total PS Installation Costs, M&S ($k): | 52.5
[37 empty] | Tech | Eng. | Elect.
[36 empty] | Total PS Installatiion Labor (hrs): | 280 | 280 | 600
[36 empty] | (man-months): | 1.75 | 1.75 | 3.75
BASIC POWER SUPPLY COSTS
|  | 4-Quadrant Switch Mode PS Costs |  |  |  |  | SM POWER SUPPLY QUOTES | [8 empty] | For a single Power System, Rack and Filter | [8 empty] | For a Single power supply +/- 300 ppm regulation: | [10 empty] | For a Single power supply +/- 100 ppm regulation:
|  | M&S COSTS | $k | kW |  |  |  | Manufacturer | Volts | Amps | Power | Cost | $/watt |  |  | 480 VAC Contrls | 1.3 | 1 | 1.3 | late 2010, early 2011 reqs |  |  |  |  | LEM (1 kamp) | 0.3 | 1 | 0.3 | late 2010, early 2011 reqs | [6 empty] | DCCT (1kamp) | 1.6 | 1 | 1.6 | late 2010, early 2011 reqs
|  | Ferm-built 65amp/150volt | [8 empty] | (kW) | $k |  |  |  | Inductors | 0.5 | 2 | 1 | Eng Estimate |  |  |  |  | DAC | 0.2 | 1 | 0.2 | late 2010, early 2011 reqs | [6 empty] | DAC | 0.2 | 1 | 0.2 | late 2010, early 2011 reqs
|  | 10kW | 4 | 10 |  |  |  | Magna-Power | 20 | 1000 | 20 | 11.8 | 0.59 |  |  | Caps and Res. | 0.5 | 1 | 0.5 | Eng Estimate |  |  |  |  | DAC Card | 0.4 | 1 | 0.4 | late 2010, early 2011 reqs | [6 empty] | DAC Card | 0.5 | 1 | 0.5 | late 2010, early 2011 reqs
|  | Raw power Supply | 5 | 22 |  |  |  | Magna-Power | 32 | 750 | 24 | 14 | 0.58333 |  |  |  |  | Subtotal: |  | 2.8 | ($k) |  |  |  | PC104 | 1 | 1 | 1 | late 2010, early 2011 reqs | [6 empty] | PC104 | 1 | 1 | 1 | late 2010, early 2011 reqs
[8 empty] | Magna-Power | 40 | 625 | 25 | 14 | 0.56 | [11 empty] | PLC | 0.6 | 1 | 0.6 | late 2010, early 2011 reqs | [6 empty] | PLC | 0.6 | 1 | 0.6 | late 2010, early 2011 reqs
|  | LABOR | Tech |  |  |  |  | Magna-Power | 40 | 750 | 30 | 16.4 | 0.54667 |  |  | Electrician | 1.2 | 1 | 1.2 | 17.1429 | m-hrs |  |  |  | Reg. Chassis | 0.5 | 1 | 0.5 | late 2010, early 2011 reqs | [6 empty] | Reg. Chassis | 0.5 | 1 | 0.5 | late 2010, early 2011 reqs
|  | SM Units | 3 | hrs |  |  |  | Sorenson (SG) | 40 | 375 | 15 | 9.3 | 0.62 |  |  | Power supply | 14 | 1 | 14 | late 2010, early 2011 reqs |  |  |  |  | PS Int. Chassis | 0.5 | 1 | 0.5 | late 2010, early 2011 reqs | [6 empty] | PS Int. Chassis | 0.5 | 1 | 0.5 | late 2010, early 2011 reqs
|  | Raw PSs and Rack | 50 | hrs |  |  |  | Lambda (GEN) | 40 | 250 | 10 | 5.8 | 0.58 |  |  | Rack | 2.5 | 1 | 2.5 | late 2010, early 2011 reqs |  |  |  |  | LVPSs | 0.15 | 3 | 0.45 | late 2010, early 2011 reqs | [6 empty] | LVPSs | 0.15 | 4 | 0.6 | late 2010, early 2011 reqs
|  |  | Eng | [14 empty] | TOTAL: | 20.5 | ($k) |  |  |  |  | Back Plane | 0.2 | 1 | 0.2 | Engineering Estimate | [6 empty] | Back Plane | 0.2 | 1 | 0.2 | Engineering Estimate
|  | SM Units | 3 | hrs |  | PAHSE CONTROLLED (SCR) POWER SUPPLY COSTS
|  | Design, layout, Raw PS | 40 | hrs |  |  |  | Manufacturer: | votls | Amps | Power | Cost | $/watt |  |  |  |  | LABOR | Tech | Eng | [6 empty] | Total: | 4.15 | ($k) | [8 empty] | Total (M&S): | 5.7 | ($k)
[11 empty] | (kw) | $k | [5 empty] | Assembly: | 1.5 | 0.2 | man-weeks
[8 empty] | Spang: | 75 | 1000 | 75 | 48 | 0.64 |  |  |  |  | Testing: | 0.2 | 0.1 | man-weeks | [6 empty] | LABOR | Tech | Eng | [7 empty] | LABOR | Tech | Eng
[9 empty] | 150 | 500 | 75 | 48 | 0.64 | [14 empty] | Assembly: | 1.5 | 0.2 | man-weeks | [6 empty] | Assembly: | 1.5 | 0.2 | man-weeks
[8 empty] | PO 586693, for 5 units, 2009 | [19 empty] | Testing: | 0.5 | 0.2 | man-weeks | [6 empty] | Testing: | 0.5 | 0.2 | man-weeks
[7 empty] | NOTE: Passive filter INCLUDED | [20 empty] | Installation: | 0.2 | 0.2 | man-weeks | [6 empty] | Installation: | 1 | 0.2 | man-weeks
[9 empty] | V/I Regulator : | 5 | $k ea
(Fermi disigned and built)
Note on K4: James A. Budlong x8480 06144N: See P/O # 623240 for reference
Note on N4: From the 2013 NEC Cost book via Ryan Crawford
Note on K5: James A. Budlong x8480 06144N: Using P/O # 623240 for reference with 4/0 @ 2.40 and 212 kcmils 212/2 = 106 kcmils ~ 100 kcmils or $1.20/ft
Note on M19: Calculation: M4 Magnet location along beamline - M4 enclosure starting point along beamline (88') + cable length to power supply relay racks on Accumulator side of AP30 using the retired 10' stochastic cooling penetrations and then into the retired Accumulator cable trays.
Note on M22: Calculation: Farthest left bend dipole location along beamline - M4 enclosure starting point along beamline (88') + cable length to SCR power supplies on Delivery Ring side of AP30 (NE corner of structure) + cabling in AP30 (pentration entrance to power supply load flags) Note: this assumes that we will be able to use the penetrations in that area of AP30
Note on AI22: I need some M&S in here for disconnecting, moving and reconnecting this supply from F27 to AP30. The calculation comes to 312.2K. How does 10% sound for the CDC contactor, etc.
Note on M28: Calculation: Center location of MC-1's penetrations along beamline - magnet location along beamline + MC-1 building to enclosure distance + cabling in MC-1 power supply room
Note on AI41: I need some M&S in here for disconnecting, moving and reconnecting this supply from F27 to AP30. The calculation comes to 158.6K. How does 10% sound?
Note on M49: Calculation: Center location of Mu2e's penetrations along beamline +/- magnet location along beamline + cabling in Mu2e which isn't 30 feet but more like 5-10 feet as the load cables come up from the penetration into the rack or special designed SCR supply

## Costing Summary
Power Supply Labor (Hrs)
| Planning | Implementation | Total
Electrical Engineer | 266.2857 | 665.7143 | 932
Electrical Technician | 0 | 4820 | 4820
Power Supply Installation Labor (Hrs)
| Planning | Implementation | Total
Electrical Engineer | 0 | 280 | 280
Electrical Technician | 0 | 280 | 280
M&S (k$)
Cable cost | 128.6976
Cable Installation | 82.6712
Power Supply cost | 635.6
Power Supply Installation | 52.5
Electrician - Installation | 60.486 | Electrician hours | * | 100.81
Total | 959.9548