## Caverns integration
| List of items to be discussed and finalysed before CD3a |  |  |  | last update | 2015-07-21
# | impact: | id | sub-items | description | who | interface with | notes | status | add'l notes 10 Aug
0 | Items to be monitored by EFIG | 0a | EFIG parameters | 1) Cavern Size | EFIG
|  |  | EFIG parameters | 2) Cryostat Size | EFIG
|  |  | EFIG parameters | 4) Cavern Height | EFIG
|  |  | EFIG parameters | 5) Size of the area between the two caverns used for assembly | EFIG
|  |  | EFIG parameters | 6) Detail of the area on the opposite side used for the Cryostat and Cryogenics installation | EFIG
|  |  | EFIG parameters | 7) Mezzanine design and space use, who will be responsible | EFIG
|  |  | EFIG parameters | 8) Drift size, slope including space used for services | EFIG
more detailed list
1 | Exp. Cavern dimension | 1a | distance cavern walls - cryostat metal structure | Assume to be of the order of 30 cm. Need to determine the flux of air in the gap going up or down from the ceiling of the cavern to the floor, to remove the heat coming from the rock and keep cavern floor below the cryostat above zero oC and control dew point. Need thermal a analysis, knowing the rock temperature and the gradient of temperature in the cryostat insulation. It is also needed a definition of the quality and finishing of teh cavern liner (flatness,....) | Identify expert in thermal simulations, after all requirements have been collected | Cryostat group, CF facility | a. Olga - new cryostat model submit to TC and import to Revit, b. prelim analysis made indicating convection only gap OK flow rate only, c. thermal analysis engineer TBD, (FNAL or CERN?) d. determine req for fan, e. cavern wall surface neat line + xxx - 0 | to be done | to do: VE documentation of larger cavern width vs advantages during installation/ops. Use 42" clear? How does this benefit cryostat construction and future inspection, detector commissioning troubleshooting? This does not include any space that might be needed for air flow
|  | 1b | tower pump region definition | Presently assume 3m between cavern wall and cryostat metal structure. Need a 3d model with realistic details of the cryogenics items, the access structure and the dimension of the ventilation pipes (if any) going down to the floor of the cavern | FNAL/CERN cryogenics group to provide a cryogenics model, CF to provide a 3 model of the acces and pipes based on 1a findings | Cryogenics group, CF facilty | a. Mark - model tower w/access at 4850L and fit in 3m space, b. crown/springline/hook height use Revit model import to Plant to set coordinate system | to be done | there is enough room for safety valve per MA. Correct # of pumps? Related to purity, which is still under discussion. Need CFD analysis of flow. Access for operations - stair? MN thinks there's enough room for this
|  | 1c | Concrete floor thickness and stability | need to verify the taday's assumptions on the concrete floor properties, based on the cryostat requirements. Need an estimate of the floor relative stability. We care less if the whole floor moves up at the same rate. We care more if part of the cavern can move up (down) faster than other parts. | CERN cryostat give requirements, CF group present the floor properties based on the requirements interm of dimesion, structural properties and flatness | Cryostat group, CF facility | a. Jeff - CERN has provided weight and contact area input to doc-11241 (CERN needs to author doc at 11241 from now on), b. floor flatness spec ref. ARUP in 033000 FL, c. floor structure and excavation heave ref. ARUP TDM doc-10272 | to be done | Ask Arup to model elastic deflection of concrete & rock as cryostat steel is installed, then membrane, then argon. Flatness differences can be accomodated by shimming the cryostat during installation.
|  | 1d | LAr volume (gas + liquid) | Present dimentioons of Cryostat are: L=67m 62m, W=15.1m, H=14m. Dimenzions are from the flat mambrane to the flat membrane, not the corrugation. These dimensions are based on the LBNE transversal dimensions. The length is a rescaling to get to the 10KT | DUNE TCn, EGIF | The two detectors technology systems | a. Dimitar/David M. - confirm dims remain same in new CATIA model, b. Russ - envelope in F10043159 (doc-11215) needs rev for DUNE piping control c. Jeff - new controlled cryostat model to ARUP | to be done | EJ says this size interior cyrostat dimension can be used by the FD
|  | 1e | cavern vertical dimensions | it depends on the cryogenics layout above the cryostat, the layout of the electronic racks and the space encessary fo rthe detetctor installation and APA/CPA manipulations. To be accounted also the layout and space of all services (ventilation pipes, cryo pipes, cable trays, ...) entering the cavern. here we need a full integration in 3d | DUNE TCn, cryogenics group, CF group to collect all requirements. Need 1 moth of a design engineer to provide the final layout | Cryogenics group, CF facilty, DUNE TCn | a. Jack - APA tooling and eracks model import with equipment, b. Mark - piping envelope into Plant proposed location | to be done | possible issue with electronics racks and height of cryogenics mezzanine. Are racks on top of exoskeleton or between the structural beams?
2 | Exp. Cavern EL power | 2a | Power needed during cryostat / cryogenics assembly | This is the power for the initial safety systems, lights, cranes, cryostat welding, fumes exausts systems, tests, …, includes safety power | CF to collect the requirements, appoint a person responsible for this | Cryostat group, Cryogenics group, CF facility | a. ARUP ventilation in 260500 Part 3, b. Jeff - meeting to layout requirements vs. time after SD meeting (note: cryostat #1 construction begin after Stage 4 cryostat #2 construction after Stage 5) | to be done | need routing of welding power into cryostat CF to collect reqmnts
|  | 2b | Power needed during detector assembly | This is the power for the initial safety systems, lights, cranes, detector assembly, components tests, …, includes safety power | CF to collect the requirements, appoint a person responsible for this | DUNE TCn, CF facility | a. Jack/David M. - input to doc-10647 including generator for cryostat lighting, etc | to be done | documented in Terri's spreadsheet. DUNE to review?
|  | 2c | Power needed during operation (racks, cryogenics, lights, safety, ….) | Power for the electrical rack, the cryogenics elements, the pump tower, the safety permanent installations + the necessary safety power | CF to collect the requirements, appoint a person responsible for this | DUNE TCn, cryogencs group, CF facility | a. Terri/Mark - check power in doc-10647 ARUP | to be done | need to review underground control room power reqmt + Jack's extra controls (server?) room life safety systems power documented already by Arup & Terri cryo already documented in CF power reqmnts DUNE to clarify power reqmnts for racks
|  | 2d | Total Power Needs | Need a time line of the power needs at the major steps of the construction and running as above. Can Power installation be staged? | CF facility | CF facility | a. Terri/Mark - answer total available at UG substation exceed add to doc-10647 | to be done | 1 cable to underground to electrrical room. Phasing happens as caverns are built out. This includes transformers in elec room
|  | 2e | Power quality | What fraction needs to be clean power and what not. Space necessary | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. Terri/Mark - detector and cryo-sys PLC no need for clean power add to doc-10647 | to be done | grounding & shielding plan describes what the requirement is but DUNE tech bd needs to revisit
|  | 2f | Safe power | Define UPS needs in the underground and space needed | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. Terri/Mark - determine safe shutdown of detector and cryo-sys add to doc-10647 not CF | to be done | need controlled shutdown for both detector & cryo. Related to controls. For CF 3 cubic meters space for UPS.
3 | Exp. Cavern ventilation | 3a | ventilation needed during cryostat and detetctor assembly | ventilation needs during cryostat and detetctor assembly, defined mostly be the amount of people present in the cavern and by the type of activities. Include the fumes exausts during welding | CF to collect the requirements, appoint a person responsible for this | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. Jeff - SURF total compilation w/all providing max at stages through schedule at meeting post SD ARUP vent analysis doc-11318 | to be done | cryostat completion implies building clean structure above for detector installation. Separate venitation system installed with clean room
|  | 3b | ventilation needed during Lar filling and operation | to be considered: numer of people present, the heat generated by the electronics and cryogenics, the needs in case of the a failure of one of the Liquid supply pipes/elements around/on top of the cryostat | CF to collect requirements. The CV group to provide an analysis and a model | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. ARUP vent model ref. doc-11318 b. requirements beyond AHU filtration at cryostat membrane installation and beyond, b. Mark - LBNF ODH doc-2478 is worst case with all running | to be done | cooling for racks is local.
4 | Exp. Cavern access | 4a | access to the caverns during assembly (cryo+detector) | define cleaness of the caverns in the various stages, access control?, … | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. David - confirm cryostat structure & membrane w/AHU filtration class 500,000, b. Jack - outside of tent class 500,000 by SURF is OK c. Jeff - stages analysis by ARUP in doc-11318 with door controls in doc-11284 arch drawing UG-PDR-A-401 | to be done | HEPA filters on HVAC units already for general cleanliness. Clean is expectedt to provide reqd detector cleanliness
|  | 4b | ventilation doors | define the layout of the ventilation doors during detector assembly, commissioning and operation | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | same as above | to be done | vent doors determined by CF ventilation scheme - will be in place at B.O. Need to convey what the door sizes are - or get requirements from cryo & detectors as to what they need
|  | 4c | need of a door to the lower drifts in the cavern | define the needs for the detector and cryo installation | EFIG | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. cryostat installation - not required, b. current plan for detector is not required | to be done | door will be left at lower drift/cavern interface for emergency egress, but will not be an accessway for cryo or detector
5 | Cranes facilities in the caverns | 5a | for the cryostat/cryogenics assembly | position and properties of the monorails | Cryostat group to define needs | Cryostat group, Cryogenics group, CF facility | a. CERN - hoist plan and capacity for cryostat required add to doc-11214, b. ARUP 100% will add central monorail to cavern - capacity | to be done | 3 monorails as per 100% PD plan. Center monorail will extend 3m into both east and west drifts and 5m over rock pillar. MN says is this is ok.
|  | 5b | for the detectors assembly | position and properties of the monorails and transversal beams. Show type of operations and manipulations. | DUNE TCn to define the needs | DUNE TCn, CF facility | a. CERN - monorail(s) w/transverse beams show positions and manipulations, b. Jack - APA install fixture and portable crane, c. Mark interference in detector cavern with mezzanine | to be done | JAS agrees will above statement.
6 | Clean rooms facilities | 6a | for the detetctor assembly inbetween adjacent caverns | define surface and properties, crane, storage space, | DUNE TCn | DUNE TCn, CF facility | a. Jack - class 100,000 tent w/supply air, crane as above, b. no requirement for remainder of floor to cryostat structure or membrane | to be done | only clean room impact on CF is for power. Current remnt based on microboone and is felt to be sufficient. Still need better understanding between cryostat & FD teams
|  | 6b | For the detector compoenents final test prior to installation on the surface | define needs in term of space and properties. Space for the last check just before lowering to the Pit and space needed for final cold tests near the Pit. Needs for particular services (cryogenics, power, ventilation, ..). Define last check areas on the surface and staging areas near the shaft (last cold test, possible assembly of Light Det and electronics) . | DUNE TCn | DUNE TCn, CF facility | a. Russ/Jack/Terri - no requirement for cold test near the pit space, b. Jack - existing floor layout for 15m pillar doc-11271 b. UG services as above, off-site warehouse for cryostat and detector, c. SURF - truck off-load near headframes | to be done
7 | Drift properties/usage | 7a | cryogenics pipes requirements | space and installation needs | Cryogenics group to define needs | Cryogenics group, CF facility | a. Mark - responsibility between Ross shaft and Governor's corner? b. ARUP cross-sections in doc-11284 UG Mech c. Mark - cryo-systems input to CF for drifts and caverns | to be done | cryo pipes between shaft and CUC is CF responsibility. Ok per Arup 75% dwg.
|  | 7b | Detectors services | space and installation needs for cables, pipes, …inbetween caverns and counting rooms | DUNE TCn to provide a model | DUNE TCn, CF facility | a. Terri - cavern drifts and UG Data Center elect b. Mark cavern drifts mech, c. Jim - UG Data Center space requirements into CUC need definition | to be done | TBD
|  | 7c | CF services | space and installation needs (power, ventilation, cable trays,..) | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | ARUP doc-11284 drawing ref M-706, SS-120 and SS-140 | to be done | CF takes care of this if clear space is known
|  | 7b | transport of the equiment during installation | check dimensions, curvatures, manipulations, interference with installaed services | CF to collect requirements and then to provide a dynamical simulation of the various activities. Need 3d CAD modeling | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. ARUP - Revit model design service with envelope dims by FD (ready), b. cryo-sys to comply with rev to 5487 and ARUP 75%, c. CERN - cryostat deliver to CF | to be done | cryo knows space available and will make that part of spec to vendors. Arup to run cryo objects through their 3D model.
|  | 7d | lower drifts status after excavation | define properties, eventual requirement | CF to collect requirements | CF facility | a. per ARUP dwg SS-120 at 100% | to be done | will put door at lower drift entrance for emergency egress only. No utilities in drift.
|  | 7e | usage per activity | define who is using the drifts, when and directions (ex. Cryostat on one side, detector /cryo form the other side of the cavern) | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. Jeff - logistics workshop cryostat from east and west except for cryostat #2 detector at center, and usage vs. time meeting put into ARUP stages model | to be done | TBD
8 | Shafts properties | 8a | cryogenics material to be lowered | check dimensions, curvatures, manipulations, interference with installaed services, max weights | CF to collect requirements and then to provide a dynamical simulation of the various activities. Need 3d CAD modeling | Cryogenics group, CF facility | comply with above | to be done | will provide size & weight restrictions to vendors
|  | 8b | cryostat material to be lowered | check dimensions, curvatures, manipulations, interference with installaed services, max weights | CF to collect requirements and then to provide a dynamical simulation of the various activities. Need 3d CAD modeling | Cryostat group, CF facility | comply with above | to be done | corner beams still an issue. Could use Ross shaft for delivery - complicates excavation
9 | Cryogenics/utilities central cavern | 9a | cryogenics needs | provide a first integration drawing, with space usage during operation, while building up (staged) | Cryigenics to define a model | Cryogenics group | a. Mark - cryo-sys beyond NX model F1039666 within Plant ECD? | to be done
|  | 9b | utilities needs | provide a first integration drawing, with space usage during operation, while building up (staged) for power, ventilation, safety, alarms, safe power, …. | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. ARUP dwg ref E-401 thru 404 b. Mark - account for Plant update as above ECD? | to be done
|  | 9c | Counting rooms requirements | provide a first integration drawing, with space usage during operation, while building up (staged) for racks, central DAQ, DCS, DSS, computing links, … | DUNE TCn to provide a model | Cryogenics group DUNE TCn, CF facility | a. DUNE - greatly expand on doc-11202 for requirements UG in CUC | to be done
10 | Safety equipments underground | 10a | fire | provide requirements and a model (3d, location, links,..) | CF to collect requirements | CF | a. ARUP documentation ref FP-001 thru 802 | to be done
|  | 10b | ODH | provide requirements and a model (3d, location, links,..) | CF to collect requirements | CF | a. Mark - ARUP is using ODH to date | to be done
|  | 10c | alarms system | provide requirements and a model (3d, location, links,..) | CF to collect requirements | CF | a. Jack - tie detector rack alarms into CF | to be done
|  | 10d | information system (mobile phones net, wi-fi, information panels, …) | provide requirements and a model (3d, location, links,..) | CF to collect requirements | CF | a. ARUP documentation ref T-001 thru T-801 | to be done
|  | 10E | Allowed Operation | Need to detemine what operations are allowed and what restrictions are imposed during that operation. Example: Welding? Liquid Transfer? | CF to collect requirements | CF | a. list restrictions at meeting after SD by brainstorm particularly those that drive CF design | to be done
11 | Above ground support infrastructure | 11a | material reception, buffer zones, unloading facilities | provide a model (3d, location, links,..) | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. cryostat material storage off-site b. off-load trucks and to shaft by SURF, c. UG drifts based on load type | to be done | likely space available in Spearfish & Sturgis. Would like to do this formally to local businesses. Work with local economic development group
|  | 11b | office space for users and for contractors & detector installers | provide a model (3d, location, links,..) | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. space available at SURF for trailers per 10255 (Ross), b. transition from construction to operation needs discussed at logistics workshop | to be done | anticipate remodeling Ross Dry. Need to understand # of people at what time.
|  | 11c | storage areas off campus (Rapid city, …) | provide a model (3d, location, links,..) | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. Jack - update to doc-984 and slides in doc-11271 | to be done | likely space available in Spearfish & Sturgis. Would like to do this formally to local businesses. Work with local economic development group
|  | 11d | housing | What are the plans for housing workers that are going to come for short periods (~ weeks) and for those coming for longer periods. | CF to collect requirements | CF | a. SURF review doc-11270 | to be done | discuss with economic development
12 | Underground occupancy | 12a | model usage of the underground | people as a function of time for the different activities | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. compilation as above in meeting planned after SD | to be done
|  | 12b | define safety organization | for users and contractors | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. SURF review doc-11270 | to be done
|  | 12c | emergency shelters | define size, location and availability in time | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. compile with 12a and SURF, LBNF and DUNE review doc-11270 | to be done
|  | 12d | housing infrastructure underground | for pauses, food, medical support | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. add bathrooms b. compile with 12a | to be done
13 | Cavern/detector grounding | 13a | cavern grounding | define the cavern grounding structure | CF to collect requirements | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. Terri/CF - discussion of WWM epoxy b. complete update to doc-7310 | to be done | what is required spacing - i.e., could wires wrapping rock bolt heads serve same function?
|  | 13b | cryostat grounding | define the cryostat grounding during assembly and operation | Cryostat group coll requir. | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. Terri/Marzio - complete update to doc-7310 | to be done | temp grounding capabilities needed
|  | 13c | detector grounding | define the detector grounding during assembly and operation | Dune TCn coll requir. | Cryostat group, Cryogenics group DUNE TCn, CF facility | a. Terri/Marzio - complete update to doc-7310 | to be done | need DUNE tech bd to discuss grnding & shielding, then feed back to CF reqmnt