## Slide 1
Workshop on Cryogenic Operations
Fermilab, 25-27 October 2016
MicroBooNE Experience: Operations of the cryogenic system for the Fermilab MicroBooNE Liquid Argon Neutrino detector
M. Zuckerbrot, M. Geynisman, J. Kilmer, B. Norris, R. Sanders, M. Sarychev, F. Schwartz, J. Tillman

## Slide 2: Presentation Outline
Cryogenic Requirements
System Overview
Stages of Commissioning
  Piston Purge
  Gas Recirculation
  Cooldown
  Filling
  Initial Liquid Purification
Operations
  Overview and Notes
Summary
LarTF

## Slide 3: Cryogenic Requirements
Additional Requirements:
  Reach purity requirements without cryostat evacuation
  < 20 K dT on the TPC during cooldown
  Level and pressure stability
  Sampling for contaminants
  Electrical isolation of cryogenic components from cryostat
LarTF

## Slide 4: System Overview
Recirculation/Cooldown System
  Fluitron gas compressor, 3 pass heat exchanger, Mole. Sieve
Purification System
  Cryostat: ASME cylindrical pressure vessel (30 psig)
  LAr pumps: Barber Nichols
  Condensers: 10 kW capacity
  Filtration Skids: Copper (O2) and molecular sieve (H2O)
    Can be activated and regenerated in place using hot Ar and Ar/H2 mix
  11,000 gallon liquid Nitrogen dewar: Coolant
  500 Gallon LAr Dewar: Supplies makeup gas, actuators, purges, etc…
  Gas analyzers: O2, N2, and H2O
    Multiple sample points: LAr pump discharge, post-filters, cryostat ullage/chimneys, 500 gallon dewar, etc…
LarTF

## Slide 5: System Overview
LarTF

## Slide 6: Stages of Commissioning
Commissioning Timeline
LarTF

## Slide 7: Stages of Commissioning
Piston Purge
  ~13 volume exchanges, < 10 ppm H2O, < 1 ppm N2, < 1 ppm O2
LarTF

## Slide 8: Stages of Commissioning
Gas Recirculation
  With no O2/N2 filtration, contaminants increase due to outgassing, controlled by venting through chimneys
LarTF

## Slide 9: Stages of Commissioning
Cooldown
  Temps. and system trips shown, maintained < 20 K dT
LarTF

## Slide 10: Stages of Commissioning
Cooldown
  Contamination during cooldown process shown
LarTF
-Outgassing decreases with temperature
-Venting from chimneys and replacing with cleaner gas

## Slide 11: Stages of Commissioning
Filling
  Contractual issues: Vendors hesitant to sign contract due to tight N2 requirements and aggressive schedule
  Temperature gradients: Form when the liquid level is low
    Controlled with shell heaters and bottom-up gas flow to increase convection in the ullage
LarTF

## Slide 12: Stages of Commissioning
Purification
  Did not fill through filters, started with commercial argon
  LAr purified to acceptable levels within a week
LarTF

## Slide 13: Operations
Overview of Normal Operating System
  Spare LAr pump, condenser, and filter skid
  Makeup argon from
  utility dewar ~3 weeks
  Inline PM inactive
  No active purge on
  chimney ports
  Pressure control via
  LN2 control valve on
  condenser coil inlet
  O2, N2 sampled at
  LAr pump discharge;
  H2O from ullage
LarTF

## Slide 14: Operations
Barber Nichols LAr Pumps
  Startup: Difficult to start without first bypassing the filters then slowly cooling them, likely amplified by downstream throttle valve
LAr Pump Bearing Failure
  Detected audibly
  Lower cold bearing (cage)
  ~6000 hours of operation
  Possible cause: Prior failure of
  discharge pressure transmitter
  caused pump to ramp up/down
  for several hours
  Likely caused cavitation and
  shortened bearing life
LarTF

## Slide 15: Summary
Electron Lifetime: Analysis is ongoing - 9 ms or greater
System Reliability: > 98.9% up time
LarTF

## Slide 16
Questions?
LarTF