## Slide 2: Vibration monitoring of the rotating machines of the CERN cryogenic systems
O. Pirotte
Cryogenics Group
Technology Department
CERN
7th International Workshop on Cryogenics Operations, October 25-27, 2016 Fermi National Accelerator Laboratory, USA

## Slide 3
Content
    Introduction
    Cold/hot spares strategy
    Vibration monitoring and analysis
    Set up of vibration monitoring at CERN
    Examples of vibration monitoring and analysis
    Dashboards and statistics
    Summary

## Slide 4: CERN accelerator complex
Geneva’s airport
T level | Installed capacity | # of plants
80 K | 5.2 MW | 14
4.5 K | 164 kW | 24
20 K | 60 W | 2
1.8 K | 19.7 kW | 12
300 mK | 350 mW | 1
LHC accelerator
LHC detectors
Other detectors
Other acceler.
Test areas
Central services
Standby

## Slide 5: Inventory of cryogenic installations at CERN (34)
23 cryogenic installations are part of the core infrastructure running 24/7/365 for the CERN physics reasearch program where availability & reliability are essential

## Slide 6
INTRODUCTION
  In case of breakdown of rotating machinery severe downtime can be induced : couple of days for the exchange of a motor / compressor / turbine / …
  -> Strategy is needed to ensure availability and reliability of rotating machinery :
    Redundant equipment, cold and hot spares
    Preventive maintenance : exchange or revision of components based on integrated running hours
    Predictive maintenance : anticipate issues and possible interventions to correct problems

## Slide 7
INTRODUCTION
  Inventory of rotating machinery and main critical components in cryogenic plants :
  At cryogenic temperature :
    Turbines in refrigerators
    Cold compressors / Pumps
  At room temperature :
    Motor-compressor systems (screw and piston type)
    Motor-pump systems (oil or vacuum)
CERN, Cryo-Ops 2014
-> 0 % downtime
-> Process control, cabling & electronic issues (active magnetic bearing)
    Powerful systems, generating large vibrations
      -> increased wear
      -> increased risks and collateral damages : leaks, pollution (He , environment)
    High costs in case of breakdown
    Long downtime
    Experience of severe breakdowns during LHC run 1 (see Cryo-ops 2014)
most critical
-> 88 compressors
-> 60 oil pumps + 6 Roots
At CERN

## Slide 8: LHC cryogenic warm compressors layout
LPb
MPb
HPb
LPa
MPa
HPa
LPa
MPa
HPa
LPb
MPb
HPb
LPb
MPb
HPb
LPa
MPa
HPa
LPa
MPa
HPa
LPb
MPb
HPb
S1-2
P18
S2-3
P2
S3-4
S4-5
P4
S5-6
S6-7
P6
S7-8
S8-1
P8
Aerzen
Stal
8 cryo plants
5 cryo islands
9 types of compressors:
2 Aerzen types (536aM & 536aH)
- 7 Stal types (S73_LP, S73_HP, S75, S87, S89, S93_LP & S93_HP)
Available spares (2016)
(HP/ LP)
(HP/ LP)

## Slide 9: LHC “Hot spare” solution
Configuration without one HP compressor. Similar configuration can be applied for LP stage compressors and in such case LP and MP bypasses between the cryo plants will be open.
TU4 flow
Screen from 2 sectors is connected to this refrigerator
TU1,2,3 stopped

## Slide 10: ATLAS & CMS “Hot spare” solution
Upgrade of ATLAS and CMS compressor stations during first long shutdown (LS1) period of LHC (2013-2014)
ATLAS : exchange of C2 compressor to ensure a mininimum of 400 g/s with three boosters, and new C6 compressor
CMS: new hot spare compressors

## Slide 11
  Vibration measurement techniques have been developed for rotating machinery since 1950's
  In the 1980’s, Portable Data Collectors (PDC) were introduced, combined with condition monitoring software
  Since then, there is a continuous enhancement of these products and their capabilities in parallel with development in electronics for hardware and software
  It is now possible to anticipate issues and to diagnose many problems for rotating machinery :
    Unbalance ,
    Misalignment, soft foot,
    Bearing faults,
    Structural looseness or resonance,
    Belt drive faults,
    Gear faults,
    Electrical motor faults (rotor bars, eccentricity rotor/stator)
    Hunting Tooth Frequency (FHT), …
  A set of specialized standards is available : ISO, VDI, API
Vibration monitoring and analyis

## Slide 12
Measurements of only global acceleration/behavior of the motor-compressor systems (1 measurement point, 0-1000 Hz)
Predictive maintenance and compressor station at CERN
Occasional use of vibration meters to check components (compressor, pipework, valve, …)
2007 2008 2009 2010 2011 2012 2013 2014 2015 2016
2007 : purchase of a first PDC (Emerson™ CSI 2130) in view of LHC run (numerous CPs, higher vibrations)
Dec-2010 QSCB-4-CP6 Roller bearing (breakdown)
VMY536aH
Dec-2009 QSCB-8-CP3 Roller bearing (failure)
VMY536aH
Jun-2011 QSCB-8-CP7 Roller bearing (breakdown)
VMY536aH
Feb-2011 QSCA-2-M08 Journal bearing (failure)
2008 - 2011
Investigations with a vibration expert
2011 - 2012
Set up of a predictive maintenance plan based on vibration monitoring
2012 - 2014
Condition based maintenance for screw compressors, roots and oil pumps and the associated electrical motors
2013 - 2016
Before 2007
Dec-2011 QSCB-8-CP6 Plain bearing (wear)
VMY536aH
Feb-2012 QSCB-4-CP7 Damaged rotor VMY536aH
Nov-2012 QSCA-8-M08 Journal bearing (wear)
Jun-2014 ANRS Roller bearing (breakdown) Kaeser

## Slide 13
Measurement points for a compressor system
Tri-Axis Sensor
Fixed coded pin
Notes:   Database setup, for every system :
  Inventory of all characteristics to configure the condition monitoring software and its database (kinematic chain, geometry, bearing data, …)
  Monitoring program : selection of all the measurement points and their characteristics (freq. ranges, resolution, …)
  Define the alarm thresholds for the various faults
  Define the measurement intervals
  Define and configure routes in the PDC
  Equip each systems with fixed coded pins to avoid measurement errors

## Slide 14
Vibration analysis
Wear
Roller / plain / journal bearing
Weakness
Unbalance (1 x n)
Rotor bars (motor)
Alignment (2 x n)
Asymetric magnetic field (2 x f.net)
Skid (resonance, Looseness)
Vibration analysis
Problems which may evolve more or less rapidly
Problems which, if corrected, will improve the system
…
…
Avoid breakdown
Higher reliability and availability, lower wear and maintenance costs

## Slide 15: Example 1 : roller bearing QSCB-4-CP6 (VMY536aH, April 2015)
(Aerzen’s expertise 29 July 2015)
(Compressor major overhauled 2 years ago!)
Assembly error during major overhauling

## Slide 16: Example 2 : roller bearing QSCB-8-CP1 (VMY536aM, 2015)
Jan-2015 : First indication of bearing issue
Jan-2016 : Exchange of the compressor during end of year shutdown
The inner ring shows two small flaking areas, a large number of overrolled indentations caused by soft and large, but also hard micro-particles, as well as abrasive removal of the machining pattern in the ball path. A large number of wear marks are visible which are either round or have the shape of circle segments, with surface distress on the bottom and which were overrolled in operation (Figs. 2 to 13). In addition to one flaked are, the machining pattern was worn off due to vibration with the bearing stationary.
SKF report (bearing after 1 year)
~1 year
Only one spare and concern with other CP of the same type

## Slide 17: Example 3 : journal bearing QSCA-8-M08 (2012)
Detection of a faulty journal bearing in a motor (August 2012) :
  « Internal play in the journal bearing is increasing slowly but continuously over last few months »
-> Replacement of the bearing during a technical stop in November 2012

## Slide 18: Example 4 : vibration analysis & alignment practice
During the set up of the vibration monitoring, many problems of misalignment were reported
Investigation wrt alignment practice. Findings :
  Configuration errors in the database (geometry, length,…)
  Faulty soft foot check
  Thermal growth not taken into account
  Dynamic tolerances not well taken into account
Alignment at "cold"
Verification at "warm"
Geometry of the system
-> Complete review of the alignment procedure and QAP
Laser shaft alignment system : OPTALIGN®

## Slide 19: Example 5 : maintenance practice & Quality Control
Alignment issue found on compressor QSCA-2-CP5 (Feb-2016)
Investigations -> alignment during Jan-2016
Thermal growth not taken into account during alignment process
Before alignment
Alignment problem
After correct alignment, and thermal growth taken into account
Vibration analysis contributes valuably and efficiently to QC
Correct alignment improves bearing and seal life, and reliability of rotary machinery
1xn before shaft seal intervention
Balancing issue found on motor QSCA-4-M0A (Feb-2016)
Investigations -> there was an exchange of shaft seal during Jan-2016
Bad remounting of coupling (unsymmetrical mounting of the conical clamping ring)
1xn after shaft seal intervention

## Slide 20: Example 6 : Operation practice (Jan-2016)
During a vibration measurement, very high vibrations are recorded for the oil pump QSCB-18-2P640 (motor & pump) : cavitation
Vib. level of pump QSCB-18-2P640
Motor
Heavy impacts
Pump
Investigation of the operation process
Vibration measurement
MP @ 2.5 bar
MP @ 3.5 bar
Comparing vibration behavior at different pump suction pressure
Vibration analysis contributes valuably to operation practice
Slide valve @ 13%

## Slide 21
Vibration monitoring : detailed dashboards
Motor status
Compressor status
Skid

## Slide 22
Vibration monitoring : dashboards & statistics

## Slide 23
Vibration monitoring : dashboards & statistics
Chart: Number of noted bearing issues
| Screw compressor with bearing issue | Motor (CP) with noted bearing issue
LHC-run 1 | 11 | 5
LHC-run 2 | 8 | 3

## Slide 24
SUMMARY
  Vibration monitoring of rotary machinery is the first brick of the predictive maintenance plan for CERN cryogenic plants
  It is a complementary and an essential tool to cold/hot spares strategy and preventive maintenance : it allows to anticipate issues and program interventions during technical stops, to prioritize the issues, and in case of urgency to switch to a hot spare configuration or to stop before the destruction of the machine
  Vibration monitoring has allowed to revise major overhauling intervals and reduce preventive maintenance costs. Nevertheless major overhauling can not be skipped (slide valves, plain bearing,…)
  Vibration analysis is a powerful tool for the QC. It was shown that it contributes to improve efficiently the maintenance and operation practices
  Vibration monitoring increases the confidence in the equipment health status and increases the availability and reliability of the cryogenic plants
  Next steps :
  Incorporate oil analysis
  Monitoring of plain bearings
  Investigate online monitoring
Thank you for your attention

## Slide 25
Additional slides

## Slide 26: Example : Rotor bars in motor (QSCA-4-M02, 2015-2016)
March 2015 -> March 2016
Sep/2015: Detection of a problem with rotor bars in motor QSCA-4-M02 (Alert: high vibration due to an asymmetry in the magnetic field)
Mar/2016 : Constant fault threshold
-> Replacement of the motor during the technical stop of May 2016

## Slide 27: Example : maintenance practice & Quality Control
Alignment issue found on compressor QSCA-2-CP5 (Feb-2016)
Investigations -> alignment during Jan-2016
Thermal growth not taken into account during alignment process
Before alignment
Alignment problem
After correct alignment, and thermal growth taken into account
> max 0.06
Soft foot issue detected for QSCA-4-CP3 (Feb-2015)
Investigations -> alignment during Jan-2015
In alignment report, one foot was found out of tolerance
Soft foot issue
Extract from alignment report in the DB
Vibration analysis contributes valuably and efficiently to QC
Correct alignment improves bearing and seal life, and reliability of the CS

## Slide 28: Vibration measurement : displacement probes
Results for shaft centerline
Despite big progress with the alignment practice, vibration analysis was continuously reporting an alignment problem for one type of compressor system (Stal S87/S89)
Noncontact displacement sensors were used to measure the displacement and shaft vibration
Compressor shaft moves horizontally 110 μm to the right
Big influence of thermal growth : 90 μm
Motor shaft moves ~57 μm up and 4 μm to the left
No influence of the thermal growth
and for dynamic measurements
Unfiltered orbit of compressor (green) and motor (blue)
Motor bearing heavily preloaded in MY

## Slide 29: Example : Unbalancing after shaft seal intervention
1xn before shaft seal intervention
1xn after re-balancing intervention
Balancing issue found on motor QSCA-4-M0A (Feb-2016)
Investigations -> there was an exchange of shaft seal during Jan-2016
Bad remounting of coupling (unsymmetrical mounting of the conical clamping ring)
After shaft seal intervention, increase of motor overall values
1xn after shaft seal intervention

## Slide 30: Example of Operation Deflection Shape measurement
A set of high stage compressors (Stal S93) was presenting very high vibration level (global). High sensitivity wrt operation conditions (MP/HP ratio)
Can we improve the system and its dynamic behavior ? -> ODS measurement
Deflection @ 398 hz
Deflection @ 49 hz
Deflection @ 49 Hz – Oil pump
Excessive vibration of oil pump and support beam
Deflection @ 199 Hz – frame
Excessive deformation of the support frame
Outcome:
Oil pump has been installed on a separate frame
Frame and pipework support need to be re-inforced (stiffness & fixations)

## Slide 31
  A set of specialized standards is available : ISO, VDI, API
Condition Based Maintenance for CS
VDI 3836 for screw compressor
ISO 18816-3 for electrical motor
ISO 18816-7 for pump

## Slide 32: Vibration analysis AMS suite – Machinery Health Manager

## Slide 33
Preventive maintenance (Cryo-Ops 2014)
Screw compressors major overhauling |  | 
Manufacturer | Recommendation | CERN preventive plan
Aerzen | 20'000 h | 40'000 h
Stal | 40'000 h | 
Kaeser | 40'000 h | 
Mycom | 20'000 h | 
Howden | 4 years of operation | 
Motors major overhauling |  |  | 
Type | Voltage | Power | CERN preventive plan
Ball bearings | 3.3 kV | - | 30'000 h
Journal bearings |  |  | 40'000 h
Ball bearings (oil pumps) | 400 V | > 10 kW | 30'000 h
 |  | ≤ 10 kW | Replacement (new)
Pumps major overhauling |  | 
Manufacturer | Recommendation | CERN preventive plan
IMO | 16'000 h | 24'000 h
Stal | 5'000 h | 24'000 h
Desmi | 8'000 h | 8'000 h
Kral | 40'000 h | 40'000 h
Mayekawa | 40'000 h | 40'000 h
Allweiller | 16'000 h | 40'000 h
Leybold | 20'000 h | 40'000 h
Major overhauling periods have been revised according to criticality criteria wrt process, redundancy, cost, available spare, and predictive maintenance plan

## Slide 34
Vibrations

## Slide 35
Set up of vibration measurements
  Database setup, for every system :
  Inventory of all characteristics to configure the condition monitoring software and its database (kinematic chain, geometry, bearing data, …)
  Monitoring program : selection of all the measurement points and their characteristics (freq. ranges, resolution, …)
  Define and configure routes in the PDC
  Equip each systems with fixed coded pins to avoid measurement errors
  Define the alarm thresholds for the various faults
  Define the measurement intervals