## Slide 1
Steve Dixon
DOE Independent Project Review of PIP-II
15 November 2016
Conventional Facilities

## Slide 2: Steve Dixon
PIP-II Associate Project Manager for Civil Construction
Relevant Experience
  Licensed Architect;
  Project Management Professional (PMP);
  LEED Accredited Professional;
  24+ years at Fermilab;
  NOvA Project L2 Manager for Site and Buildings;
  General Plant Project Manager
    Short Baseline Neutrino (SBN) Near Detector Building;
    Short Baseline Neutrino (SBN) Far Detector Building;
    CDF Refurbishment;
    Experimental Operations Center;
Charge Item: #4

## Slide 3: Outline
Construction Phase Scope of Work
R&D Phase Goals
R&D Status
R&D Schedule to Complete
IIFC Interface
Summary

## Slide 4: Construction Phase Scope of Work
Conventional Facilities to Support PIP-II:
  Site Work
    Utilities (electrical, communication, ICW, DWS, sanitary, chilled water);
    Site Improvements (roads, parking area, hardstands, tank foundations);
  Linac
    Below Grade Enclosure;
    Linac Service Building;
  Transport Line
    Transport Line Enclosure;
    Beam Absorber Enclosure;
    Connection to existing Booster;
  Cryo Plant Building
  Mechanical Plant
Charge Item: #2

## Slide 5: R&D Phase Goals
Conceptual Design:
  Conceptual Design Report Text;
  Conceptual Design Drawings;
Life Safety Analysis
Support Analysis of Alternates
Support NEPA Process
Prepare for CD-1
  R&D Phase resource loaded schedule
  Construction Phase resource loaded schedule
Prepare for CD-2/3a
  Advanced Preliminary Design for Site Prep work
  Advanced Preliminary Design for Cryo Plant Building

## Slide 6: R&D Phase Goals and Status
Conceptual Design:
  Conceptual Design Report Text; - Draft Complete
  Conceptual Design Drawings; - 95% Complete [1]
  Life Safety Analysis - Draft Complete [2]
  Support Analysis of Alternates – Complete
  Support NEPA Process - Ongoing
  Prepare for CD-1 – Ongoing
  R&D Phase resource loaded schedule - Complete
  Construction Phase resource loaded schedule – Ongoing
  Prepare for CD-2/3a – Not started
  Detailed Design for Site Prep work
  Detailed Design for Cryo Plant Building
  [1] – Conceptual Design Drawings can be found in TeamCenter ED0005473
  [2] – Draft LSA can be found at PIP-II-doc-120
Charge Item: #1
Charge Item: #1
Charge Item: #5
Charge Item: #2

## Slide 7: Conceptual Design Process
Meetings with Stakeholders:
  Goal: Document the spatial and infrastructure requirements for PIP-II facilities;
  Started in January 2016;
  Product was the Conceptual Design drawings and text;
Results:
  Developed cooling strategies for pulsed mode and continuous wave operation;
  Conventional facilities are similar to typical Fermilab construction;
  Backup material has additional details

## Slide 8: R&D Status – Overview
Cryo Plant
Utility Building
Linac
Transport Line
Booster
Beam Absorber
Tevatron

## Slide 9: R&D Status – Siting Considerations
Site Plan with Possible Future Expansion
Existing Utilities
and Services
Accommodating Future Expansion:
Siting;
Space in Linac for additional cryomodules;
Stub for Linac extension;
Stub for beamline to Muon Campus;
Location of Cryoplant
Size of Linac Enclosure (ongoing)

## Slide 10: R&D Status
Looking Southeast From Wilson Hall
AZero Service Building
Linac
Tevatron Enclsoure Berm
Linac Service Building
Cryo Plant Building
Utility Building
Surface Building Massing
Looking South Along Beamline
White Flags = Warm Components
Blue Flags = Cold Components

## Slide 11: R&D Status Typical Linac Cross Section
Cryo Zone
1’-10”
Aisle
1’-10”
Aisle
RF Zone
LCW Zone

## Slide 12: R&D Status – Linac Plan
Cross Section Looking South at Waveguide Penetrations
Cross Section Looking South at Coax Penetrations
Public Participation: Viewing Gallery

## Slide 13: R&D Status – Main Ring/Transport Line

## Slide 14: R&D Status – Transport Line/Booster
Looking Northeast Towards Booster Tower East
Excavation Plan at Booster Tower East
Booster Tower West
Shielding Upgrade - 1998

## Slide 15: R&D Status – Cryo Plant
Warm Compressor Station
Cold Box Station
Tank Farm
Risk: Cryoplant induced ground motion and superconducting cavity detuning. LCLS-II Engineering Note [3] recommended distance (30m) and isolated foundations for compressors.
  [3] – Engineering Note LCLSII-4.8-EN-0326-R0 can be found at PIP-II-doc-122
68m (225’)
Distance to Linac

## Slide 16: R&D Status – Utility Building

## Slide 17: R&D Status – Support NEPA
Site Plan with 2016 Wetland Delineation
Charge Item: #5
Construction Stockpiles
V. Kuchler

## Slide 18: R&D Phase Schedule to Complete
FY17:Select an Architect/Engineer;
  Update the drawings;
  Refine cost estimate;
FY18:Begin Detail Design for Site Prep package
FY19 : Final Design begins (includes Site Prep)
Notes: Conceptual Design:
  Update the Conceptual Design Report Text;
  Complete the Conceptual Design Drawings;
Incorporate Life Safety Analysis Recommendations;
Support NEPA process;
Continue to refine and document requirements;
Select an Architect/Engineer;
  Update the drawings;
  Refine cost estimate;
Prepare for CD-1
Prepare for CD-2/3a
  Advanced Preliminary Design

## Slide 19: IIFC Interface
Accommodate the cryo plant equipment
Interface is with Cryogenics Department (Arkadiy)
Charge Item: #4

## Slide 20: Summary
Technical Design is based in iterative discussions and meetings with stakeholders and the conceptual design of the conventional facilities can meet the specified technical performance requirements;
The scope of the conceptual design for the conventional facilities is sufficiently well defined to support the preliminary cost and schedule estimates;
The cost estimate will be refined in the coming month as part of the early tasking of the architect/engineer (A/E);
To date, the conventional facilities portion has been accomplished by a combination of in-house staff supplemented with consultants. This effort will continue with an A/E firm in FY17;
Conventional facilities has been involved with ES&H activities to date and will continue to be in the coming stages;
The IIFC interface for the conventional facilities is primarily the cryo plant and this interface is well defined;

## Slide 21
Backup Material

## Slide 22: Stakeholders:
Fermilab:
Alessandro Vivoli, Anindya Chakravarty, Anthony F Leveling, Arkadiy L Klebaner
Beau F. Harrison, Curtis M. Baffes, David E Johnson, David W Peterson
Don Cossairt, Donald V Mitchell, Emil Huedem, Jim Niehoff, Fernanda G Garcia
Jerry R Leibfritz, Jerzy Czajkowski, John E Anderson Jr, Luisella Lari
Matthew Quinn, Maurice Ball, Paul Derwent, Ralph J Pasquinelli
Todd M Sullivan, Valeri A Lebedev, William A Pellico
Consultants:
Tom Lackowski, TGRWA
Ron Jedziniak, LG Associates
Rick Glenn, Jensen Hughes

## Slide 23: Meeting Minutes (PIP-II-doc-70)
01 - Coordination Meeting - 17FEB16 (pdf)
02 - Cryogenic Department Meeting 19FEB16 (pdf) – Cryo Meeting
03 - Coordination Meeting - 02MAR16 (pdf) – Linac Enclosure
04 - Coordination Meeting - 09MAR16 R1 (pdf) – Linac Enclosure and Cooling
05 - Coordination Meeting - 24MAR16 R1 (pdf) – Linac Enclosure and Cryo Plant
06 - Cryo Coordination Meeting - 01APR16 (pdf) – ICW Cooling and Cryo
07 - Coordination Meeting - 14APR16 (pdf) – Penetrations and Cooling Strategy
08 - Coordination Meeting - 28APR16 (pdf) – Cooling Strategy
09 - Coordination Meeting r1 - 12MAY16 (pdf) – Shielding and Transport Line
10 - Coordination Meeting - 09JUN16 (pdf) – Shielding Summary
11 - Coordination Meeting - 07JUL16 (pdf) – RF Distribution and LCW Cooling
12 - Coordination Meeting - 21JUL16 (pdf) – High Bay Equipment
13 - Coordination Meeting - 04AUG16 (pdf) – Cryo Summary and Linac Gallery
14 - Coordination Meeting - 15SEP16 (pdf) – Sitewide Electrical Distribution

## Slide 24: Drawings (TeamCenter ED0005473)
54 Drawings
One (1) General sheet
Six (6) Civil sheets
Forty-Three (43) Architectural sheets
Three (3) Mechanical sheets
One (1) Electrical sheet

## Slide 25: Typical Design Basis Sheet

## Slide 26: Preliminary Shielding Considerations
6’
17.5’
7.5’
18.5’
18.5’
(transport line and absorber)
Preliminary Shielding Depths shown below. Further analysis required, especially at the Booster.
Thanks to D. Cossairt, T. Leveling and M. Quinn
Used the 10W/m curve for the conceptual design

## Slide 27: Cryo Plant
Warm Compressor Station
Cold Box Station
Tank Farm

## Slide 28: Cryo Plant

## Slide 29: Cryo Plant Cooling Requirements
Water Requirements
  1,200 – 1,500 gpm flow
Pond System
  Chemical characteristics met by Pond system;
  Solids content characteristics NOT met by Pond system;
  No Pond - ~$500-$700k per acre;
ICW System
  Chemical characteristics met by existing ICW system;
  Solids content characteristics NOT met by ICW system;
  Sampling ICW;

## Slide 30: Cryo Plant – Water Quality Requirements
Thanks to A. Klebaner and A. Chakravarty

## Slide 31: Cryo Plant – Water Quality Test Stand
BZero Compressor Building
Installed as part of the Mu2e Cryo work for CDF;
Installed test ports to sample the ICW before and after the strainer;
Includes a Adams strainer with “standard” slot sizes (baseline);
Two month rental of a Lakos strainer to reduce the solids;
Replacement filter elements in Adams strainer with smaller slot size;
Arranged for FESS/O water testing service to increase the testing to include solids;
Scheduled testing on same duration as CUB;
Compare strainer options with water quality requirements.
Strainer
Port for Rental Strainer
Port for Rental Strainer

## Slide 32: PM vs. CW Considerations
Driven by duty factor of the equipment
  15% for Pulsed Mode
  100% for Continuous Wave Mode
Common For Both Modes
  Physical arrangement of heat producing equipment;
  Electrical power supply (not usage);
  Conventional Facilities handles the heat load to air (HLA);
Difference is Primarily Cooling
  5.0 mw in pulsed mode;
  10.5 mw in continuous wave mode;

## Slide 33: PM vs. CW Considerations - Cooling
Heat Loads |  |  |  |  |  |  |  |  |  |  |  | 
 |  |  | Pulsed Mode (MW) | Continuous Wave Mode (MW) |  |  |  |  |  |  |  | 
Low Conductivity Water (LCW) |  |  | 1.65 | 7.07 |  |  |  |  |  |  |  | 
Cryoplant Cooling (Cryo) |  |  | 3.4 | 3.4 |  |  |  |  |  |  |  | 
 |  | Total (MW) | 5.05 | 10.47 |  |  |  |  |  |  |  | 
 | Industrial Cooling Water (ICW) |  |  | Cooling Ponds (PW) |  |  | Towers (close) |  |  | Towers (open) |  | 
Pulsed Mode | MW to GPM Conversion |  | 682.79 | MW to Acres Conversion |  | 800kw/acre |  |  |  |  |  | 
 | LCW | 1,125 | gpm | LCW | 1.98 | acres | LCW | 1.0 | towers | LCW | 1.0 | towers
 | Cryo | 1,400 | gpm @17 Fdt | Cryo | 4.08 | acres | Cryo | 2.0 | towers | Cryo | 1.0 | towers
 |  | 2,525 | gpm |  | 6.06 | acres |  | 3.00 | towers |  | 2.00 | towers
 |  |  |  |  |  |  |  | exclude standby |  |  | exclude standby | 
CW Mode | MW to GPM Conversion |  | 682.79 | MW to Acres Conversion |  | 800kw/acre |  |  |  |  |  | 
 | LCW | 4,827 | gpm | LCW | 8.48 | acres | LCW | 4.0 | towers | LCW | 2.0 | towers
 | Cryo | 1,400 | gpm @17 Fdt | Cryo | 4.08 | acres | Cryo | 2.0 | towers | Cryo | 1.0 | towers
 |  | 6,227 | gpm |  | 12.56 | acres |  | 6.00 | towers |  | 3.00 | towers
 |  |  |  |  |  |  |  | exclude standby |  |  | exclude standby | 
 | Other Considerations |  |  | Other Considerations |  |  | Other Considerations |  |  | Other Considerations |  | 
 | Strainers, Drought Conditions |  |  | Strainers, Heat Exchangers, Treatment |  |  | Heat Exchangers, Treatment, Make Up |  |  | Heat Exchangers, Treatment, Make Up |  | 
 |  |  |  | Drought Conditions |  |  | Building Costs |  |  | Building Costs |  | 
 | Note: 1,400 gpm is the highest flow currently available from the existing ICW system |  |  |  |  |  |  |  |  |  |  | 
Thanks to E. Huedem
Basis for Estimate

## Slide 34: Cooling Design Approach
Goal: Modular approach that allows for efficient operation in both modes;
Pulsed Mode
  Heat Load to Air (HLA): Utilize chilled water from existing CUB for equipment cooling (this utilizes the available headroom at CUB);
  LCW: (1) Cooling tower
  Cryo: (2) Cooling towers
Continuous Wave Mode
  Heat Load to Air (HLA): Install a chilled water loop to supplement the pulsed mode system with (2) cooling towers;
  LCW: Add (1) Cooling tower
  Cryo: No change

## Slide 35: PIP-II Utility Building
7 Towers:
HLA: 0 in PM, 2 for CW
LCW: 1 for PM, 2 for CW
Cryo: 2 for both modes
N+1 Standby: 1
Separate Piping Runs
For PM and CW modes

## Slide 36: Mechanical Conceptual Design

## Slide 37: MV Electrical Conceptual Design