## Slide 1: FNAL pCM Cryogenic System
Jay Theilacker
pCM Testing Review Workshop
January 11, 2017

## Slide 2: Operating Modes
The CMTF Cryogenic system has two methods to achieve 2K operation in the cryomodule test stand
  Cryoplant Cold Compressors and Warm Vacuum Compressor
  (2K Refrigeration Mode, 500W capacity)
  Advantages: JT heat exchanger in plant
  Disadvantages: Min. CC flow, Less forgiving, Learning curve
  Cryoplant in Liquefier Mode with Kinney Vacuum Pump
  (Liquefaction Mode)
  Advantages: More forgiving/flexible, Better turndown
  Disadvantages: No JT HX

## Slide 3: Operating Modes
Kinney Pump
2K
Load

## Slide 4: CMTF Layout
VB
SCP
CMTS
Kinney Header
Cryo Transferline
DB

## Slide 5: pCM Cryogenic Operating History
  2K Plant
    Long recovery from CC trips (learning curve)
    Anxious for data for CM PRR
  4.5K Plant and Kinney Vacuum Pumping
    Could only achieve 2.1K due to pressure drop and high flows resulting from the lack of a JT HX
    Single cavity tests were performed in this mode
  2K Plant
    Single cavity tests at 1.93K
  Shutdown
    Addressed Kinney header ΔP, added LN2 shield cooling to DB, changed CC drives, changed one control valve, added thermal intercept to CM JT valve, added flow meter to Kinney discharge
  4.5K Plant and Kinney Vacuum Pumping
    Current mode at 2K

## Slide 6: Operational Experiences
  Apparent thermoacoustic oscillation (TAO) in CM JT valve
    Added thermal intercept, investigating valve stem wiper
  High flow rates due to high JT valve inlet temperature (no JT HX and TAO)
    Addressing TAO, investigating JT HX possibilities
  Liquid level stability in CM was challenging
    Four contributors:
      incline
        Design requirement
      high total flow rate
        See previous
      JT flow injection into two-phase pipe may be disrupting liquid surface
        Added baffle to CM2, considering increasing JT line size
      apparent flow regime in two-phase pipe not as expected in CMTS
        Researching

## Slide 7: Baffle at JT Injection

## Slide 8: Design for Increased JT Line Size

## Slide 9: Operational Experiences
  Liquid level can heaters impact level measurement
    Limit wattage, primarily use cavity heaters
  Microphonics
    Tests are in progress to identify sources (Yuriy Pischalnikov talk)

## Slide 10: Backup

## Slide 11: Operational Experiences

## Slide 12: Liquid Level Instability