## Slide 1: JLAB pCM Cooldown
Ed Daly representing the JLAB CMTF Team
pCM Workshop
11 January, 2017

## Slide 2: CMTF – pCM Testing in Progress

## Slide 3: CM Cooldown (Saga)
  15-DEC Cooldown started
    Monitored temperatures, pressures and vacuum levels
    Maintained limits on GHRP and thermal shields - Temp differences - <15 K vertical, < 50K axial
    Proceeded slower than expected due to unexpected pressure drops (1 – 2 K/hr !)
      Bypass valve in HX was suspected (Cv – 0.35)
      Qo valve in return u-tube was checked and initially ruled out
  26-DEC Collected liquid at ~ 0.055 atm (above lambda, unstable)
    Re-checked installation of Qo valve actuator installation procedure recommended by mfgr.
    Valve was partially closed - once fully opened, return pressure improved
    Vacuum levels – 1E-11 torr (beamline), 1E-09 torr (coupler), 1E-06 torr (InsVac)
    Note: vacuums have remained stable at these levels throughout testing
  28-DEC Collected liquid and controlled at ~0.048 atm (at lambda, stable)
    Stable liquid level control over several days
    Return pressure improved but capacity was still limited
    Debugged faulty liquid level readbacks
  03-JAN Achieved stable liquid level control at pressure ~0.035 atm
    Kinney pump control settings modified to improve return pressure
  04-JAN Began debugging interlocks in advance of cavity testing

## Slide 4: CM Cooldown - Observations
  Maintained limits on GHRP and thermal shield
    Need to verify mixed gas cooldown capability
  Cavity cooldown rates from 40K through Tc ranged up to 2K/min
  Magnetic field levels at cavities are very good
    ~ 1 mG average, 4.5 mG peak at one location
  LL readbacks are intermittent at times
    Possible interaction between CD & JT valves and LL behavior
    Rapid filling in upstream end before downstream end when refilling
  As at FNAL, observed high heat load on JT valve
  Cooldown rate will proceed more quickly (Target is 10K/hr)
    Unexpected pressure drops were eliminated
    Plan to use warm gas mixing during next cooldown from 300K

## Slide 5: Frosty JT Valve (courtesy of J. Nelson)
Revised design based on FNAL guidance
Flow dependent heat load
  TAO?
Ice covers brass portion at times (high flow)
Covers only top of pant leg at times (low flow)
Mitigate with fan for this round of testing

## Slide 6: Liquid Level % vs Liters (Level)
Some interesting points
  0% - 36 L; 100% - 305 L
Control at 80% for level CM
Plan to control at downstream end with sloped CM at ~90%

## Slide 7: Liquid Level Response – Cooldown from ~50K
GHRP
LL
Cav Temps

## Slide 8: JLab CMTF Bayonet Box & End Cap
4K – 2K HX (CD to AB)
Qo Valve in U-tube
Orifice between line A & B in end cap
CD valve in Bayonet Box

## Slide 9: Cooling from 40K
Need to have fast cooldown thru Tc
pCM cooled in about 6 hours from 40K to collecting liquid at 2K
Cavities thru Tc – rates are good to expel flux
Cavity temp. response GHRP cooldown temps
0.5 K/min

## Slide 10: Summary
pCM is cold and controlling at level and acceptable pressure range
Expect cooldown to proceed in 3 – 4 days
  With proper Qo valve setting
  Revised bypass valve sizing (changed in new HX)
Plan to set slope of pCM to 0.5% and check LL response