## Slide 1: PIP-II Site Power Requirements
James Steimel
PIP2MAC
11 April 2017

## Slide 2: Summary of Site Power Loads
Purpose of table is to understand peak demands of new infrastructure.
System | Wall‐Plug Power (kW)
RF Power Amplifiers | 8320
Magnets (quads, solenoids, dipoles) | 300
Support Electronics | 150
Cryogenic Systems | 3250
LCW | 200
Chilled water | 500
HVAC | 200
Conventional Systems | 300
Total | 13220

## Slide 3: RF Power Contribution
Table assumes that wall power must be capable of providing peak power of all amplifiers.
Total load assumes that amplifiers are 50% efficient at specified peak output power.
Expected pulsed operation load assumes ~15% duty cycle for RF and quiescent power at 10% of peak power.
 | Frequency (MHz) | Number of RF cavities | Number of RF amplifiers per cavity | Regime of operation | RF amplifier power (kW)
RFQ | 162.5 | 1 | 2 | CW | 75
MEBT Bunching cavities | 162.5 | 4 | 1 | CW | 3
First HWR cavity | 162.5 | 1 | 1 | CW | 3
Other HWR cavities | 162.5 | 7 | 1 | CW | 7
SSR1 | 325 | 16 | 1 | Pulsed | 7
SSR2 | 325 | 35 | 1 | Pulsed | 20
LB650 | 650 | 33 | 1 | Pulsed | 40
HB650 | 650 | 24 | 1 | Pulsed | 70
Total available RF Power: 4160kW
Total available wall power required assuming 50% efficiency: 8320kW
Total expected load for pulsed operation: ~2080kW

## Slide 4: Electrical System Contribution Assumptions
Magnets required available power assumes a slow ramp, no high inductive loads.
Support electronics assumes we need about two 20A relay racks of support equipment (LLRF, interlocks, instrumentation, etc.) for every 5 cavities.
Style | Quantity | Operating temperature | Location (quantity), comments
LEBT switching dipole magnet | 1 | warm | LEBT
LEBT solenoids | 3 | warm | LEBT
LEBT 2-plane dipole corrector | 4 | warm | LEBT
LEBT chopper | 1 | warm | LEBT
MEBT long quads | 14 | warm | MEBT
MEBT short quads | 20 | warm | MEBT
MEBT 2-plane dipole correctors | 12 | warm | MEBT
MEBT chopper kicker | 2 | warm | MEBT
HWR solenoids | 8 | cold | HWR
HWR 2-plane dip. correctors | 8 | cold | HWR
SSR1 solenoids | 8 | cold | SSR1
SSR1 2-plane dip. correctors | 8 | cold | SSR2
SSR2 solenoids | 21 | cold | SSR2
SSR2 2-plane dip. correctors | 21 | cold | SSR2
SC linac quads | 40 | warm | LB650 (2∙11), HB650(2∙4), linac extension (2∙5)
SC linac 2-plane dip. correctors | 20 | warm | LB650 (11), HB650(4), linac extension (5)
SC linac skew-quads | 4 | warm | linac extension
Transport line regular quads | 49 | warm | Arc 1 and straight (18), beam dump line (4), Arc 2 (27)
Transport line large bore quads | 2 | warm | Upstream septum
End of Booster line quads | 6 | warm | 
Transport line one-plane dip. correctors | 56 | warm | Arc 1 and straight (18), beam dump line (4), Arc 2 (33)
Transport line dipoles | 37 | warm | Arc 1 (8), Arc 2 (24), beam dump (5)
End of transport line long dipoles | 3 | warm | bend in vertical plane
End of transport line short dipoles | 2 | warm | bend in vertical plane
Fast dipole switch | 1 | warm | 
Septum magnet | 1 | warm | 
Beam dump sweep magnet | 1 | warm | 

## Slide 5: Cryogenic System Power Estimates
Cryogenic heat load based on calculated heat load from CDR shown in the table.
Final number of 3.25MW from cryogenic engineers based on historical inefficiencies of pumps and cooling.
Circuit | Estimated Heat Load [W]
2K return | 248.7
4.5K supply | 77
LTTS return | 60
HTTS supply | 90
HTTS return | 576

## Slide 6: Water and Air Cooling
LCW and Chilled Water(RFQ) sections of the table only include power required for pumps.
HVAC power estimate only includes power to maintain building temperature due to weather fluctuations.
Power table still needs to be updated to include cooling load for equipment. (~2 MW for pulsed operation and ~8.4 MW for CW operation).

## Slide 7: Issues to be Resolved
Need to quantify water cooling power and where cooling power is absorbed by current utilities.
Need to quantify HVAC cooling power considering heat load to air in enclosures (power amplifiers, cooling pipes, input coupler exhaust).
Need to analyze cleanliness of power lines required. Will harmonic filters be required for CW and/or pulsed operation?
How many systems will require UPS backup (SRF cavity tuner motors)?