## Slide 1: PNNL Pressure Safety Program Overview
2017 NLDC ES&H Working Group Meeting
Eric G. Damberg
Worker Safety & Health Division Manager
Richland, WA
Notes: Photo Title Slide Design #06 with SILVER Background
To best incorporate the contents of this title slide into your presentation(s), be sure to use the Select All command (Ctrl+A) before choosing to Copy (Ctrl+C) the content and then Pasting (Ctrl+V) it onto the title slide location within your new or existing PowerPoint file.

## Slide 2: Program Overview
PNNL Pressure Safety requirements applies to systems operated by F&O and R&D organizations in the following categories:
Pressurized equipment and systems
Compressed gas equipment and systems
Cryogenic equipment and systems
Vacuum equipment and systems

## Slide 3: Pressure System Categories
System Type | Definition | Pressure Permit Required
Facility system | Systems or vessels that are the responsibility of F&O to maintain and operate. (e.g., boilers, process water etc.) | No
Vacuum system | Any system that is operated at negative gauge pressures (i.e., below standard atmospheric pressure). | Yes if >13 liters
Pressurized glassware | A glass system or component that is intended for use, or could possibly be pressurized, above 2 psig, or has a stored energy greater than or equal to 1,000 foot-pounds (lbf-ft). | Yes
Action required vessel and systems | A vessel or system that has a stored energy greater than 1,000 lbf-ft. (e.g., Parr bombs and autoclaves less) | Yes (PNNL fabricated) NO (Commercial OTS)
Minimal action | A system or vessel where the system’s stored energy is less than 1,000 lbf-ft. | No

## Slide 4: Graded Approach to ASME B31 Implementation in Research
Pilot Scale Research System
ASME B31 Codes Applied
Lab Scale Research System
NFPA 45 Applied
  Design methods follow ASME B31 and Boiler and Pressure Vessel codes
ASME B31.3 is applicable to:
“..piping that is typically found in petroleum refineries, chemical, pharmaceutical, textile, paper, semiconductor, and cryogenic plants, related to processing plants and terminals.”
NFPA 45 scope for laboratory piping:
  “…apply to laboratory buildings, laboratory units, and laboratory work areas….”
OSHA 29CFR1910.1450:
“Laboratory Scale means work with substances in which the containers used for reactions, transfers, and other handling of substances are designed to be easily and safely manipulated by one person. Laboratory Scale excludes those workplaces with a function of producing commercial quantities of materials.”
Notes: Laboratory Scale: Work with chemicals in which the containers used for reactions, transfers, and other handling of chemicals are designed to be easily and safely manipulated by one person.
Note: A similar definition is included in OSHA 29CFR1910.1450: “Laboratory Scale means work with substances in which the containers used for reactions, transfers, and other handling of substances are designed to be easily and safely manipulated by one person. Laboratory Scale excludes those workplaces with a function of producing commercial quantities of materials.”
Code applicability:
ASME B31.3 is defined as “piping that is typically found in petroleum refineries, chemical, pharmaceutical, textile, paper, semiconductor, and cryogenic plants, related to processing plants and terminals.” ASME B31.3 specifically states that “This code prescribes requirements for materials and components, design, fabrication, assembly, erection, examination, inspection, and testing of piping.” Nine different categories of requirements are uniquely identified as being addressed by the code.
The scope of NFPA 45 as it relates to laboratory piping is:
  This standard shall apply to laboratory buildings, laboratory units, and laboratory work areas, whether located above or below grade, in which chemicals, as defined, are handled or stored.
- Design methods are based on ASME B31 and Boiler and Pressure Vessel codes
- NO Owner / Owner’s Inspector or NDE requirements implemented for lab scale

## Slide 5: ASME B31 Owner and Owner’s Inspector Requirements for Research Systems
Laboratory Scale Category & Codes |  | Owner’s Inspector Requirements
ASME B31.1 | Pilot / Engineering Scale | Owner’s Inspection and Pressure Permit Required
ASME B31.3 |  | 
ASME B31.5 |  | 
NFPA 55 |  | 
NFPA 54 |  | 
NFPA 45 | Laboratory Scale (> 1,00ft-lbs Stored Energy) | Obtain PNNL Pressure Permit
 | Laboratory Scale (< 1,00ft-lbs Stored Energy) | Follow PNNL Work Practices
Owner and Owner Inspector Roles
Delegated to Battelle by DOE Pacific Northwest Site Office