## Slide 1
Accelerator Division Status
Duane Newhart
All Experimenters’ Meeting/Lab Status Meeting
15 May 2017

## Slide 2: Accelerator Operations Summary
From: May 08, 2017 (0000 hours)
To: May 15, 2017 (0000 hours)
Calendar Week # 19
NuMI Weekly Integrated Intensity 1.64 E19 protons
Beam Hours To NuMI 150.4 hours
BNB Weekly Integrated Intensity 1.15 E19 protons
Beam Hours To BNB 157.7 hours
NMuon Weekly Integrated Intensity 4.20 E16 protons
Beam Hours To NMuon 145.0 hours
MTest Weekly Integrated Intensity 2.09 E13 protons
Beam Hours To MTest 70.0 hours
MCenter Weekly Integrated Intensity 6.80 E12 protons
Beam Hours To MCenter 130.2 hours

## Slide 3: NuMI Beam Power
635.6kW NuMI with SY => 700 KW NuMI only
1 hour beam power record: 715.88 kW (1/25/17 20:25 to 21:25)

## Slide 4: NuMI Operation

## Slide 5: BNB Operation

## Slide 6: Complex Status
LINAC
  Running well
Booster
  Running well
MI/RR
  MI52 vacuum
    Plagued with vacuum issues again
NuMI
  Focusing on staying above 641kW with Switchyard running
Booster Neutrino Beamline (BNB)
  Running well
Switchyard
  MTest, Mcenter, SeaQuest
Muon Campus Commissioning
    8 GeV beam around the Delivery ring
    Began On Target Operation late last week
      3 GeV secondaries into the ring
General
  Downtime
    May 15th
      ComEd Switch 2002 repair
  Shutdown Planning
    Preparing to adjust schedule

## Slide 7: ComEd Switch 2002: 345kV feed to MSS
During thermal scans ComEd found that one phase of the switch is hot, about 200 F. Further investigation showed the contact for the hot phase is not seated properly an is only making contact with about 50% of the conductor. The risk of course is the contactor may fail either by continuing to overheat or just open.

## Slide 8: Current Plan: Monday, May 15th
0600: Turn Accelerators/Controls/Cooling off.
0630-0700: Transfer Master Substation loads to Kautz Road Substation
  30 minute outage for Master Substation loads
0700~1500: ComEd repairs/replaces switch
1630: CUB Cooling off, Controls down
1700-1730: Transfer Master Substation loads from Kautz Road Substation
  30 minute outage for Master Substation loads
1800: Turn on begins
This scenario allows the switch to be repaired, and for the site to continue being fed from two 345kV lines, L11120 & L14419.
MSS powers the majority of the site!
KRS powers MI buildings and currently Feeder 46A (A0 Cryo Compressors)

## Slide 9: MI-12 Communication Duct
Summary
Emergency Repair Plan In Place
  Need 2 hour notification
  Vendor has cable
New Communications Duct Plan
  Communications duct installation
    New duct installed
  New fiber cable has been delivered
    Electricians notified
    Installation pending
  Hope to move to new cable in March
    Coordinate downtime with Master SubStation outages
Damaged on 10/24/16
Protected from further damage
Provides timing/date to Neutrino Experiments
Experiments running fine

## Slide 10: PIP-II Injector Test & FAST Status
PIP-II Injector Test
  Shutdown
    Install full of MEBT
      4th week of 6-10 week shutdown
FAST
  300 MeV beamline construction continues:
    300 MeV quadrupoles were valved into the LCW system.
      2 quads had leaks on braze joints; mitigated the leaks.
    The beamline is currently pumping down from 441 to 609.
    The key cores were installed in the interlocked gates and doors.
    The Cave will become ODH Class 1 this week.
      Cave will go from Open Access to Supervised Access
    Magnet checkouts should begin next week.
    A newly purchased UHV rated sapphire window failed leak check.
      The window is for a 300 MeV synchrotron radiation experiment so a smaller window was located our A0 inventory. It is going through leak check now.
    The beamtube was connected from the 50 MeV line to the Cryomodule and aligned.
      The remaining beamtube section left to install is the beryllium window spool piece at the high energy absorber.
    The fast-acting valve test and installation will occur this week.

## Slide 11: CMTS1 Status
LCLSII Prototype Cryo Module
  F1.3-02.
    Ran the entire cryomodule (8 cavities + magnet package) at nominal voltage (>128 MV) and current (20 A) for several hours with no issues.
      Q0 was measured on each cavity.
    LLRF and microphonics were studied.
    Currently the cryoplant is off due to power outages.
      It is expected to cool back down Tuesday,
      resume operation as soon as practical, and complete testing by week's end.

## Slide 12: Schedules and Links
Schedule can be accessed from the Operations Department Home Page
  Schedules -> Operations Schedule
Direct link to schedule
  http://www-ad.fnal.gov/ops/schedule.html

## Slide 13: Collaborations / Partnerships / Members [22pt Bold]