## FSCF requirements
ID | Type | Parents | Object Heading | Object Text | Rationale | Notes | Reference | Old ID | Old Parents
FSCF-Engr-115 | requirement | FDmod-gen-001, FDmod-gen-002, FDmod-gen-003, cryostat-003, cryosys-001, cryosys-002, cryosys-003, | Far Detector Conventional Facilities | The FSCF shall provide conventional facilities that include spaces for Far Detector modules and for Cryogenics Equipment and systems to construct and operate the Far Detector |  | This is stated here so that a proper interface document can be prepared. |  | fscf-l2-prog-12
FSCF-Engr-001 | requirement | cryostat-005, cryostat-041 | AHU's | FSCF shall provide AHU(s) underground as needed to meet air-quality requirements. |  |  |  | FSCF-Engr-19 | FD-engr-14
FSCF-Engr-002 | requirement | cryostat-005 | Air ducting in caverns | FSCF shall provide air ducting to avoid interference with the monorail cranes |  |  |  | FSCF-Engr-15b
FSCF-Engr-003 | requirement | cryostat-018 | Anchorages on rock septum for bridge support | FSCF shall provide anchorages into rock for cryostat supplied bridges to be placed between each cryostat and the septum to allow future access to top of cryostat | Anchorage to the rock pillar and/or the side walls to support a bridge of whatever size necessary for the detector assembly. | Need load requirements from cryostat |  | FSCF-Engr-10b
FSCF-Engr-004 | requirement | Cryosys-074 | Booster Compressor Cooling | FSCF Shall provide 100 kW cooling capacity to each of (4) nitrogen booster compressors through use of a liquid to liquid heat exchanger. | The heat load estimates are available in docdb-251. | The cryogenics group provides the "hot" side plumbing. | Docdb-251 | FSCF-ENGR-65
FSCF-Engr-005 | Requirement | Glo-prog-2 and 3 | Cable fire rating | FSCF shall provide all cable to meet code and be low smoke zero halogen. The low smoke zero halogen requirement can be omitted if cable is completely enclosed and smoke from a burning cable cannot escape into occupied space. Any variance to this requirement shall be communicated to the LBNF/DUNE ESH Manager for discussion with the SURF ESH Director and the Fermilab AHJ. | There are three categories of cable installation placement modes: riser, installed vertically; plenum, installed in an air supply plenum space; and general. By code, cable must meet the fire rating associated with where it is installed. LBNF will have cable installed vertically and, by code, it must be riser rated. LBNF does not anticipate any cable being installed in air supply plenums; therefore, all other cables must meet the code requirements for general. In addition, SDSTA requires that all cable be low smoke zero halogen | Resolve ARUP recommendations with AHJ |  | FSCF-Engr-X11
FSCF-Engr-006 | requirement | cryostat-033 | Cavern Height | FSCF shall ensure that the detector cavern extends vertically above the 4850 L, a minimum distance from the bottom of the monorail support beams as defined in drawing F10043159. Also, the vertical distance from the bottom of the monorail beam to the top of the pit concrete floor slab shall be consistent with the minimum distances as shown in drawing F10043159. | To provide adequate clear space for rigging and lifting components. | Per EDMS identifier 1551658 (LBNF Cranes Requirements) | Drawing F10043159 (docdb 464), | FSCF-Engr-4c
FSCF-Engr-007 | requirement | cryostat-036 | Cavern Moisture | FSCF shall provide drainage and sumps sufficient to prevent standing water accumulation on cavern slabs on grade. Visible moisture appearing after the application of shotcrete does not require mitigation. | The interior of cavern shotcrete walls and concrete slabs on grade shall provide systems to manage water penetration to inner surfaces. Some moisture is acceptable and will be managed locally by the experiment as necessary. | required by all Far Site LBNF/DUNE |  | FSCF-Engr-9 | FD-engr-10
FSCF-Engr-008 | requirement | FDmod-gen-017 | Cavern Walls, Concrete Floor, Cryostat and Far Detector Electrical Grounding | FSCF shall provide separate grounding systems between the detector/associated DAQ system and the balance of the facility. These systems shall be isolated using inductors. Non-conductive reinforcement shall be provided in the detector cavern side walls and in the detector cavern floors. | Due to the 600 electron noise limit, the power supplied to the front end electronics and the DAQ system located on the top plate of the cryostats will require a power/ground system which is electrically isolated from cavern power/ground. A controlled safety ground will be installed between cavern and detector ground. Electrically isolated Ufer Ground systems will be installed for each of the four cryostat pits and the upper space of the detector hall - no conductive paths (rebar, anchors, etc.) shall connect these isolated systems. | required by DUNE Far Detector. Do the rock bolts have to be non-conductive? | doc-285 | FSCF-Engr-29 | FD-engr-16, LArFD-L2-se-7
FSCF-Engr-011 | requirement | FDmod-gen-026, glo-prog-003 | Central Rock Platform, air-tight isolation | FSCF shall provide air-tight isolation below the rock septum floor elevation between the two detector module chambers in a cavern, both during excavation phasing and after construction. | This protects cryostat construction during excavation and ensures that an issue with one detector does not affect another during operation. | required by DUNE Far Detector; Rock septum will be used. |  | FSCF-Engr-10 | FD-engr-11
FSCF-Engr-012 | requirement | FDmod-gen-001, cryostat-037, cryostat-038 | Central Utilities Cavern Space Allocation | FSCF shall construct the Central Utilities Cavern with space allocated for a control room, DUNE data room, CF mechanical, electrical and plumbing systems and Cryogenics Systems | Far Site Conventional Facilities allocates spaces according to its own requirements, Far Detector requirements and Cryogenics Systems requirements. | required by DUNE Far Detector, LBNF Conventional Facilities and LBNF Cryogenics Systems | Interface drawing F10061421, Docdb-4070 | FSCF-Engr-12 | FD-engr-3, FD-engr-4, FD-engr-5
FSCF-Engr-013 | requirement | cryostat-020, cryostat-042 | Chamber slab on grade surface Tolerances | FSCF shall Provide OVERALL FF=25 (approximate +/- ¼ inch) and FL=20 (approximate +/- 5/16-inch) with LOCALIZED FF=17 (approximate +/- 3/8inch) and FL=15 (approximate +/-3/8inch) in compliance with ACI 117, 4.8.5 as determined by the ASTM 1155 test procedure | This means that that maximum point deviation from the assumed datum or elevation is +/- 3/8 inch and the maximum stacked or cumulative deviation is also +/- 3/8 inch |  | Docdb-1784 | FSCF-Engr-11 | FD-engr-13
FSCF-Engr-015 | requirement | cryosys-002, cryosys-003, FDmod-gen-004 | Component Delivery to chambers | FSCF shall design facility geometry to allow delivery of equipment and materials as follows: All cryostat components shall be delivered from the Ross shaft to the east and west ends of the detector caverns. All detector components shall be delivered from the Ross shaft through the central detector cavern accesses, including passing through the CUC. All equipment to be used in the CUC shall be delivered through either the east end of the CUC or the central drift leading to CUC. |  | The far detector components are found in docdb-3051. The cryostat components in CERN EDMS 1531746, v.1 | Docdb-3051 | FSCF-Engr-55c
FSCF-Engr-016 | assumption | FDmod-gen-022 | Components Delivery Access (surface) | SURF shall provide space for a forklift to lift off a container up to 8' x 8'6 x 40' of Far Detector components from delivery trailers directly to the Ross Headframe according to the planned delivery schedule. | The clean TPC components will be delivered to the site in clean trailer or container trucks. | required by DUNE Far Detector |  | FSCF-Engr-39 | FD-engr-17
FSCF-Engr-017 | requirement | cryosys-041, cryosys-042, cryosys-044 | Compressor Heat Exchangers - 1 (surface) | FSCF shall provide a fluid-based cooling system to remove heat from the nitrogen compressors supplied by the cryogenics group, including all plumbing to connect the system to the compressors. |  |  |  | FSCF-Engr-51
FSCF-Engr-018 | requirement | cryosys-041, cryosys-042, cryosys-044 | Compressor Heat Exchangers - 2 (surface) | FSCF shall provide redundancy in the cooling system to allow maintenance to be performed on the system without shutting down more than one compressor at a time |  |  |  | FSCF-Engr-51a
FSCF-Engr-019 | requirement | cryosys-041, cryosys-042, cryosys-044 | Compressor Heat Exchangers - 3 (surface) | FSCF shall design the cooling system to allow operation of 0-4 compressors in all weather conditions |  |  |  | FSCF-Engr-51b
FSCF-Engr-020 | requirement | cryosys-041, cryosys-042, cryosys-044 | Compressor Heat Exchangers - 4 (surface) | FSCF shall design the cooling system to manage heat from up to four (4) Emerson VSS3001 compressors |  |  | Doc 259 | FSCF-Engr-51c
FSCF-Engr-021 | requirement | cryostat-005, cryostat-041, Cryosys-046 | Condensation | FSCF shall ensure a minimum of 15,000 cfm per detector module or one air change per hour per cavern for both detector caverns (four chambers) and the CUC | Analysis work indicates that this will prevent condensation formation along the bottoms and sides of the cryostats |  | DUNE docdb-519 | FSCF-Engr-15a
FSCF-Engr-022 | requirement | cryosys-003 | Cryo building -1 | FSCF shall provide space adjacent to the compressor building for five (5) 114" diameter x 466" tall dewars, four for LAr, one for N2 |  | Need info from cryo on spare space for additional dewars |  | FSCF-Engr-49a
FSCF-Engr-023 | requirement | cryosys-003 | Cryo building -2 | FSCF shall provide space adjacent to the compressor building for five (5) 5' x 6' x 14' tall vaporizers, with 4' clearance on all sides, four for argon, one for nitrogen. |  |  |  | FSCF-Engr-49b
FSCF-Engr-024 | requirement | cryosys-003 | Cryo building -3 | FSCF shall provide space for a 6' x 6' purity checking building, supplied by cryo, adjacent to the LAr dewar |  |  |  | FSCF-Engr-49c
FSCF-Engr-025 | requirement | cryosys-047 | Surface Compressor Building HVAC | FSCF shall provide the LBNF Surface Compressor building with an HVAC system to ensure air temperature within the range from 40-104 degrees Fahrenheit. |  | required by LBNF Cryogenics Systems |  | FSCF-Engr-45 | FD-engr-4, FD-engr-5, FD-engr-17
FSCF-Engr-026 | requirement | cryosys-002 | Cryogenics Building | FSCF shall provide a surface building to accommodate LBNF cryogenics equipment and associated infrastructure. |  | required by LBNF Cryogenics Systems | doc-248 | FSCF-Engr-43 | FD-engr-4, FD-engr-5, FD-engr-17
FSCF-Engr-027 | requirement | cryosys-005 | Cryogenics piping | FSCF shall provide (2) 16" nitrogen gas pipes (Low pressure), (2) 8" nitrogen gas pipes (high pressure) and (1) 8" argon gas pipe from the trench entrance at the compressor building through the Ross shaft to the associated cryogenics-supplied equipment in the CUC | Per cryogenics design | The gas pressure ratings are as follows: 8” GN2 at 200 psig, 16” GN2 at 50 psig and 8” GAr at 75 psig each |  | FSCF-EGR-25a
FSCF-Engr-029 | requirement | cryosys-003, cryosys-051 | Cryogenics Systems Space and Mounting | FSCF shall provide appropriate mounting systems for the pipes in the caverns and in the drifts |  | required by LBNF Cryogenics Systems. Locations TBD | Docdb-3393 | FSCF-Engr-26 | FD-engr-3, FD-engr-4, FD-engr-5
FSCF-Engr-030 | assumption |  | Cryostat Perimeter Volume Hazard Designation | The space between the cryostat sides and the rock walls is not considered occupied space. | LBNF Conventional Facilities has no responsibility for this requirement. LBNF cryostat and cryogenics system is responsible for analysis and hazard designation. | required by DUNE Far Detector, LBNF Cryostat and LBNF Cryogenics Systems for inspection and maintenance. The access will be limited by administrative controls before and after filling. |  | FSCF-Engr-17 | FD-engr-14, 15
FSCF-Engr-033 | requirement | Cryostat-004 | Detector Cavern Dimensions | FSCF shall ensure that the detector Cavern width, height and length are in agreement with drawing F10043159 | Cryostat size plus minimum 1 foot clear space annulus defines minimum cavern size |  | Drawing F10043159 (docdb 464) | FSCF-Engr-4a
FSCF-Engr-034 | requirement | FDmod-gen-017 | Electrical Power - Detector and Central Utilities Caverns | FSCF shall provide separate shielded transformers and gear for the detector electronics and general circuits in order to minimize electromagnetic interference. |  | required by DUNE Far Detector |  | FSCF-Engr-27 | LArFD-L2-se-7, FD-engr-16
FSCF-Engr-035 | requirement | cryosys-004, cryosys-005 | Electrical Power Cryo Building | FSCF shall ensure that the LBNF Cryogenics surface building accommodates electrical power type and capacity set by cryogenics. |  | required by LBNF Cryogenics Systems | doc-208 | FSCF-Engr-48 | FD-engr-4, FD-engr-5, FD-engr-17
FSCF-Engr-036 | requirement | FDmod-gen-001, cryosys-001, cryosys-057 | Electrical Power Distribution | FSCF shall provide electrical power distribution in the caverns to meet FD and cryo systems needs |  | required by DUNE Far Detector | doc-208 | FSCF-Engr-31 | FD-engr-15
FSCF-Engr-037 | requirement | cryosys-043 | Equipment Structural/foundation support in CUC | FSCF shall satisfy equipment support requirements, such as weight and footprint of cryogenics equipment (compressors, turboexpanders, dewars, etc.) and detector DAQ equipment including racks in the CUC. |  |  | DUNE docdb-248, 259 | FSCF-ENGR-58
FSCF-Engr-039 | requirement | FDmod-gen-019 | Far Detector Caverns Orientation | FSCF shall ensure that the Far Detector caverns are aligned to within +/- 1.0 degree of the Fermilab beam as measured in a 4850L horizontal plane. | The tolerance value is intended not to be finer than can be achieved by precision engineering survey. | This should trace back to DUNE Far Detector requirement. The beam azimuth (clockwise) from true North in global coordinate system is Az = 287-43-10.96596 deg-min-sec. |  | FSCF-Engr-3 | glo-sci-17, FD-engr-2, FD-engr-3
FSCF-Engr-041 | requirement | FDmod-gen-016 | Far Detector Installation | FSCF shall ensure that a portion of the area above the rock septum, a volume defined as 14.4m W x 5m H x 10m L, with the 14.4 m side aligned with the cavern transverse centerline, shall remain clear of utilities to allow installation of a temporary clean room. | Cannot have any utilities passing through this space to allow installation of the clean room. | Have Bill Miller, Jack Fowler validate this requirement (1/12/17: no progress yet on validating these dimensions; hoping for info by summer 2017 -JF). Need a new clearance envelope drawing. Check with Matt 10/30/2017. The numbers seem feasible (11/2/2017) | Drawing F10043159 (docdb 464) | FSCF-Engr-19a
FSCF-Engr-042 | Requirement | FDmod-gen-017 | Fiber cable tray grounding | FSCF shall provide a cavern grounding system for the grounding of all cable trays | This allows separate grounding scheme for the detector components and the fiber cable trays |  |  | FSCF-Engr-X10
FSCF-Engr-043 | Requirement | Cryosys-033, FDmod-DAQ-008 | Fiber cable tray location | FSCF shall provide unistruts in the caverns for cable trays | This will allow easy access to the mezzanine components | Locations TBD |  | FSCF-Engr-X9
FSCF-Engr-044 | Specification |  | Fiber Connector Specification | FSCF shall provide fiber connectors at both the surface data room and the underground data room for each fiber using MTP/MPO connectors (mass connector, up to 48 per connection). | Needs verification method
FSCF-Engr-045 | Requirement | FDmod-daq-008 | Fiber Count Expansion Capability | FSCF shall provide means to allow for expansion to up to 960 total fibers (480 pairs) along both routes through the Ross and Yates. | Allows for Dual Phase Option, which requires 96 pairs per detector, while retaining the original 96 pairs |  |  | FSCF-Engr-X3
FSCF-Engr-046 | Specification | FSCF-Engr-045 | Fiber Data Rate | FSCF Shall provide fiber meeting a minimum specification of G.652 | Provides capability to support 100 Gbps
FSCF-Engr-047 | Parameter | FSCF-Engr-045 | Fiber for Detector Data | FSCF Shall provide a minimum of 15 fiber pairs per detector (60 pairs total) for data | Based on assumed data compression within CUC, comfortable number
FSCF-Engr-048 | Parameter | FSCF-Engr-045 | Fiber for Detector Slow Control | FSCF Shall provide a minimum of 1 fiber pair per detector (4 pairs total) for slow control | Each detector requires independent control
FSCF-Engr-049 | Parameter | FSCF-Engr-045 | Fiber for FSCF | FSCF Shall provide a minimum of 4 pairs of fiber for FSCF use. | 1 BMS, 1 Fire, 1 GPS, 1 Miscellaneous
FSCF-Engr-050 | Parameter | FSCF-Engr-045 | Fiber for GPS | FSCF shall provide a minimum of 2 fiber pairs for GPS timing | Based on experience at MINOS
FSCF-Engr-051 | Parameter | cryosys-053 | Fiber for LAr | FSCF shall provide a minimum of 4 pairs of fiber for use by LAr cryogenics
FSCF-Engr-052 | Parameter | cryosys-053 | Fiber for LN2 | FSCF shall provide a minimum of 4 pairs of fiber for use by LN2 cryogenics. |  |  |  | FSCF-Engr-X12
FSCF-Engr-053 | Requirement | FDmod-daq-008, cryosys-048, FDmod-gen-024 | Fiber Infrastructure | FSCF shall provide fiber from the surface data room (connected to the SURF network) to the underground data room using only fusions splices, with ends terminating into connectors only, within the CUC and the Surface Data Room | fusion splices limit attenuation |  |  | FSCF-Engr-X1
FSCF-Engr-054 | Parameter | FDmod-gen-025, cryosys-053 | Fiber or SURF Network | FSCF shall provide a minimum of 2 pairs of fiber for general access to the SURF based network. These fibers may connect to the SURF network at the 4850L | These will be used for internet network connection, either via wall jacks or WAP's
FSCF-Engr-055 | Requirement | FDmod-daq-008 | Fiber Spare Capacity | FSCF shall provide redundant fibers for data, GPS, and slow control via both the Ross Shaft and Yates Shaft | Allows quick recovery from damaged fiber through one route. |  |  | FSCF-Engr-X2
FSCF-Engr-057 | Requirement | glo-prog-2 | Fire and life safety control station | FSCF shall provide space in the underground control room for a control station with monitors and keyboards, etc for fire and life safety
FSCF-Engr-058 | requirement | FDmod-comm-003, fscf-l2-prog-3 | Fire Suppression Systems | FSCF shall provide fire-suppression sprinklers in the Far Detector caverns of the pre-action type for protection of the electronics. |  | required by all Far Site LBNF/DUNE during Projects. pre-action type is required by DUNE Far Detector during operations to reduce risk of damage to equipment |  | FSCF-Engr-20 | FD-engr-15
FSCF-Engr-059 | requirement | cryosys-005 | Gas pipe arrangement | FSCF shall arrange all gas piping (with adequate spacing) so as to allow maintenance/replacement of pipe sections without removal of any other pipe. | To allow maintenance without interfering with other (or redundant) systems. |  |  | FSCF-EGR-25c
FSCF-Engr-060 | requirement | cryostat-003, cryostat-018 | Height of Cryostat | FSCF shall ensure that the elevation of the top of the warm cryostat structure will be located at the 4850L +/- a distance defined by cryostat in the warm condition (prior to cooldown) | The +/- vertical tolerance should be driven by equipment roll-on/roll-off capability | Need more info |  | FSCF-Engr-??
FSCF-Engr-061 | requirement | cryostat-005 | HVAC systems | FSCF shall maintain the Far Detector chambers at a temperature between 67 to 85 degrees F, a relative humidity level between 15 and 85 percent, and a maximum dewpoint of 48 F | Temperature and RH range set by environmental requirements for computers and worker comfort. Maximum dewpoint set to keep moisture from condensing on the cryostat or electronics racks. | required by DUNE Far Detector and LBNF cryostat |  | FSCF-Engr-16 (FOR SURF) | FD-engr-14, 15
FSCF-Engr-062 | requirement | cryosys-004, cryosys-005 | Industrial Water Cryo Building | FSCF shall ensure that the LBNF surface cryogenics building accommodates an industrial water supply capacity of 10 gpm. |  | required by LBNF Cryogenics Systems |  | FSCF-Engr-46 | FD-engr-4, FD-engr-5, FD-engr-17
FSCF-Engr-063 | requirement | cryostat-035, cryosys-054, FDmod-gen-028 | Industrial Water at 4850L-CUC | FSCF shall provide industrial water to the north central entrance of the CUC at the 4850L to accommodate 10 gpm. | A nominal amount of water will be required for wash down of parts and replenish equipment supply. | required by DUNE Far Detector, LBNF Cryostat, and LBNF Cryogenics Systems |  | FSCF-Engr-22 | FD-engr-15
FSCF-Engr-064 | requirement | cryostat-035, cryosys-054, FDmod-028 | Industrial Water at 4850L-caverns | FSCF shall provide industrial water to each detector module chamber at the 4850L to accommodate 10 gpm.
FSCF-Engr-065 | assumption |  | Lavatory Facilities | Lavatory facilities shall be provided by SURF in or adjacent to the Far Detector Hall to accommodate cryostat, cryogenics systems and far detector construction occupancy rates. |  |  |  | FSCF-Engr-53
FSCF-Engr-066 | requirement | FDmod-gen-017 | Lighting | FSCF shall install no lights that incorporate ballast or spark circuits in or within 50' of the Far Detector Caverns due to EMI considerations. | Due to EMI considerations, the 600 electron noise limit, and relatively thin tank wall, Avoid all types of lighting that use ballast or spark start circuits. | required by DUNE Far Detector |  | FSCF-Engr-33 | LArFD-L2-se-7, FD-engr-16
FSCF-Engr-067 | requirement | fscf-l2-prog-3 | lighting levels | FSCF shall provide a minimum lighting level of 50 foot candles (500 Lumens) in the control room, conference room and office spaces and 40 foot candles (400 Lumens) elsewhere |  |  | BSI Prelim Design Report docdb 136 | FSCF-Engr-33a
FSCF-Engr-068 | requirement | cryosys-055 | LN2 Dewars space | FSCF shall provide space for (24), approximately, 1.45m diameter x 9.0m long LN2 dewars at the 4850L |  | to be located as far downstream in the air exhaust path as possible. The size, shape and fit, pending final design. Reference drawing F10061421 in docdb-4070 | Reference drawing F10061421 in docdb-4070 | FSCF-ENGR-64
FSCF-Engr-070 | assumption |  | Material Radioactivity | Materials used in FSCF construction do not have to be specified to minimize background radiation levels. | Naturally occurring background radiation levels in concrete and other construction materials do not exceed the levels in the soil and rock, and therefore low-radioactivity construction materials are not needed. |  |  | FSCF-Engr-14 | FD-engr-13
FSCF-Engr-071 | requirement | cryosys-027, cryosys-076 | Mezzanine support | FSCF shall provide attachment point for the mezzanine platform for installation of proximity cryogenics in each chamber and also provide lifting eyes in the crown over the mezzanine as per requirements specified by cryo systems |  | Load details provided in docdb-464 | DUNE docdb-464 | FSCF-ENGR-59
FSCF-Engr-073 | Requirement | FDmod-comm-001, Cryostat-034, cryosys-049 | Monorail Controls | FSCF shall ensure that the monorails are equipped with radio controls that provide individual or simultaneous controls for the 3 monorails, i.e. all 3 or a combination of 2 shall be wirelessly controlled simultaneously | This is a wireless control mechanism that will prevent interferences during travel of hoists | More details to come after Conveyance workshop December 2017
FSCF-Engr-074 | Assumption | Cryostat-034 | Monorail Design | The lifting beam and the spool piece design shall be provided by cryostat taking into consideration the space availability | Due to restricted space availability an optimal design of the beam and spool piece is necessary
FSCF-Engr-075 | Requirement | FDmod-comm-001, Cryostat-034, cryosys-049 | Monorail Extension | FSCF shall ensure that the monorails extend 3m into the eastern-most and western-most drifts to facilitate loading of the cryostat pieces, and that they extend over the rock septum to the extent shown in the minimum clearance definition drawing F10043159. |  |  | DUNE docdb-464
FSCF-Engr-076 | Requirement | FDmod-comm-001, Cryostat-034, cryosys-049 | Monorail Height Capacity | FSCF shall ensure that monorail hoists are equipped so that the hook reaches the floor of the detector pit. | This is necessary to provide maximum flexibility of use.
FSCF-Engr-077 | Requirement | FDmod-comm-001, Cryostat-034, cryosys-049 | Monorail Hoist Power | FSCF shall ensure that all hoists are equipped with back-up power capable of supplying power for 10 minutes in the event of a power failure | If the power goes out while a load is in the air, the hoists should operate to allow load to be lowered to the ground in a safe manner
FSCF-Engr-078 | Requirement | FDmod-comm-001, Cryostat-034, cryosys-049 | Monorail Hoists Capacity | FSCF shall ensure that two sets of three monorail hoists each have a minimum capacity of 15 metric tons (16.54 US short tons). | These two sets are to be installed in caverns 1 and 2. Hoists for caverns 3 and 4 will be provided at a later date; however, monorail beams shall be provided in all four caverns. This capacity provided by cryostat takes into account the weight of the largest piece to be assembled. The intent is that IF multiple hoists operate on the same beam the minimum design capacity of 15 metric tons is not exceeded.
FSCF-Engr-079 | Requirement | FDmod-comm-001, Cryostat-034, cryosys-049 | Monorail Hoists Operation | FSCF shall ensure that monorail hoist motors have a heavy (H5) duty cycle | This is due to possible 24 hrs/day, 7 days/week, multiple year initial usage planned
FSCF-Engr-082 | Requirement | FDmod-comm-001, Cryostat-034, cryosys-049 | Monorail Power Supply | FSCF shall ensure that the monorails are provided with a shoe-style power supply strip that runs along the length of the monorail beam | The shoe-style power supply will help prevent interference caused by the use of festoon power supply wires during travel
FSCF-Engr-083 | Requirement | FDmod-comm-001, Cryostat-034, cryosys-049 | Monorail Quantities | FSCF shall ensure that each excavated chamber is equipped with 3 monorail beams, the locations of which shall be as specified in the minimum clearance definition drawing F10043159 | This quantity is needed for the installation of cryostat pieces
FSCF-Engr-085 | assumption |  | Personnel Occupancy | SURF shall accommodate a maximum LBNF/DUNE personnel underground occupancy of 50 during concurrent cryostat construction, cryogenics system construction and Far Detector installation. LBNF/DUNE campus occupancy shall be 4 during operations. | Concurrent activities is required to increase schedule efficiencies. Occupancy rates may require temporary refuge facilities or certain activities suspended. | required by DUNE Far Detector and LBNF Cryostat and Cryogenics Systems |  | FSCF-Engr-5 | FD-engr-8
FSCF-Engr-086 | requirement | cryosys-005 | Gas Piping Safety | FSCF shall install all cryogenic gas piping so as to avoid potential damage from traffic. | To avoid potential damage from traffic. |  |  | FSCF-EGR-25b
FSCF-Engr-088 | assumption |  | Shop Space | There will not be dedicated space for a temporary machine shop at 4850L; Far Detector, cryostat and cryogenics systems will plan and negotiate use of available space to accommodate their installation activities. | LBNF Conventional Facilities has no responsibility for this requirement. The shop space will be required during the installation of the FD cryostat and cryogenics system. | required by LBNF Conventional Facilities to limit excavation |  | FSCF-Engr-8 | FD-engr-9
FSCF-Engr-093 | Requirement | FDmod-gen-023 | Surface data transfer room | FSCF shall provide a surface data transfer room with space, power (30 kVA), and cooling for a minimum of 6 data racks |  | Requirements need to be clarified by DAQ group (June 2017). This is per Eric James direction 7/13/2017 |  | FSCF-Engr-X6
FSCF-Engr-094 | assumption |  | Surface Site Security | The existing facility security fencing with locked gates prevents unauthorized personnel from accessing surface facilities including cryogenic equipment. No additional fencing is required. | Uncommon safety hazards exist in these areas and the public must be kept safe. |  |  | FSCF-Engr-40 | FD-engr-17
FSCF-Engr-095 | requirement | FDmod-gen-017 | Transformer Shield | FSCF shall provide power transformers that come with double faraday shields to all Far Detector Front End/DAQ Electronics in order to satisfy noise limit. | Due to the 600 electron noise limit, the power supplied to the front end electronics and the DAQ system located on the top plate of the cryostats will require a power/ground system which is electrically isolated from building ground. A controlled safety ground will be installed between building and detector ground. | required by DUNE Far Detector |  | FSCF-Engr-32 | FD-engr-15, 16
FSCF-Engr-096 | requirement | cryosys-003, cryosys-004 | Truck Access at fill stations | FSCF shall ensure that the space is available for the fill station cryogenic dewars to accommodate two cryogen tractor-trailer delivery units simultaneously. | The delivery of liquid argon for filling the detector is a critical path schedule item. As such, provisions need to be made for multiple deliveries at the same time. Liquid cryogen transport trailers without tractor are 2.5 m wide x 10 m long x 3.3 m high and weigh 44,000 kgf. | required by LBNF Cryogenics Systems |  | FSCF-Engr-38 | FD-engr-17
FSCF-Engr-097 | requirement | cryosys-004, cryostat-032, FDmod-gen-022 | Truck Site Access | FSCF shall ensure that the site construction accommodates access by standard WB-67 over-the-road transport tractor-trailers. Any restrictions regarding weights of trucks, wheel loads, axle loads, etc will be governed by state, county and local ordinances for bridges and roads and should not show up as an LBNF requirement because all designs must comply with all federal, state, and local laws and ordinances. |  | required by DUNE Far Detector, LBNF Cryostat and LBNF Cryogenics Systems |  | FSCF-Engr-37 | FD-engr-17
FSCF-Engr-108 | requirement | Cryostat-035 | Waste Water Cryo Building | FSCF shall ensure that the LBNF surface Cryogenics building accommodates water drainage capacity of 10 gpm. | Waste water is composed of water, rock sediment, and at times during construction, non-toxic, biodegradable cleaner such as Simple Green. Power washer capacity typically less than 4 gpm. | required by LBNF Cryogenics Systems |  | FSCF-Engr-47 | FD-engr-4, FD-engr-5, FD-engr-17
FSCF-Engr-109 | requirement | Cryostat-036 | Water Drainage Far Detector Caverns | FSCF shall ensure that the Far Detector caverns have water drainage capacity of 10 gpm plus natural ground water infiltration rate | This water is composed of water, rock sediment, and at times during construction, non-toxic, biodegradable cleaner such as Simple Green. Power washer capacity typically less than 4 gpm. The water drainage capacity of 10 gpm does not account for fire suppression system discharge which should be reconsidered during design. (this may be required for cryo) | required by LBNF Cryostat |  | FSCF-Engr-23 | FD-engr-15
FSCF-Engr-111 | Requirement | FDmod-gen-025, cryosys-048 | Wireless Connectivity | FSCF shall provide wireless connectivity to the SURF network for general use in the path from the Ross Shaft to all three main caverns, including all entrances to each cavern except the mucking ramp |  | This is a communications requirement not a fiber requirement. Need clarification if this could be deemed to supersede the scope option for leaky feeder. 10/30/2017: Ask Jack regarding this item. TBD later |  | FSCF-Engr-X8
FSCF-Engr-112 | requirement | FDmod-gen-016 | Clean room | FSCF shall make available a space with sealed concrete surfaces on the rock septum to accommodate the Far Detector group's construction of a class 100,000 clean room. | The clean room environment inside the detector caverns, enveloping the cryostat loading area will be supplied by the Far Detector group. | required by LBNF Conventional Facilities to limit cost, DUNE Far Detector is responsible for environmental regulatory and contamination class conditions within its installation clean room environment. Check the class of the clean room and verbiage of this requirement. |  | needs number; was fscf-l2-prog-14
FSCF-Engr-114 | requirement | glo-prog-004 | Surface Grade | FSCF shall ensure that the grade of any surface used for transport does not exceed 15%.
FSCF-Engr-117 | requirement | FDmod-gen-017 | Isolated Ground | To mitigate noise, FSCF shall ensure that no conductive/copper connections of any phone or network system are made to the isolated detector ground in the Far Detector Hall. | Conductive connections to building ground is acceptable. If phones are to exist on or near Cryostat (near DAQ installation), VoIP (Voice over Internet Protocol) should be implemented with fiber optics.
FSCF-Engr-118 | Specification | glo-prog-014 | Noise Abatement (surface) | FSCF shall ensure that cryogenic equipment noise is reduced to a maximum 55 dB building exterior noise level for equipment located on the surface. | This is a "joint" requirement for CF and Cryo, since it can be solved by either insulating the building or the compressors
FSCF-Engr-119 | Specification | glo-prog-002 | Secondary Containment (surface) | FSCF shall provide the FD Cryogenics building with secondary containment capacity | Oil filled machinery requires secondary containment capability. Cryosys expects to handle 220 gallons of oil for each of the 4 nitrogen screw compressors.
FSCF-Engr-121 | assumption |  | Parking | The facility shall provide space for parking of 4 cars in proximity of the control room during the operations phase of the detector.
FSCF-Engr-122 | requirement | Cryosys-034, Cryostat-049, FDmod-gen-029 | Components geometry and weight | FSCF shall accommodate components from detector, cryostat and cryogenics in the shaft as a cage or slung load as per size and weight constraints described in docdb-328 |  |  | Docdb-328
FSCF-Engr-123 | requirement | FDmod-comm-002 | Underground experimental work area | FSCF shall provide an underground experimental work area within the underground control room that will be able to accommodate up to 5 people/workstations |  | This is per Eric James direction 7/13/2017
FSCF-Engr-124 | requirement | FDmod-comm-002 | Underground data processing room | FSCF shall provide space for an estimated 52 racks for the DAQ systems, along with power and cooling for the racks | Number of racks are to be specified according to the DAQ model adapted. Currently estimated 50 racks for detectors and 2 racks for CF use | This is per Eric James direction 7/13/2017
FSCF-Engr-125, (TBD later, 13 July 2017) | requirement | cryosys-050 | Underground cryogenics work area | FSCF shall provide an underground cryogenics work area within the underground control room that will be able to accommodate up to 4 people/workstations |  | This is per David Montanari direction 7/13/2017
FSCF-Engr-127 | requirement | Cryosys-075 | Lifting eyelets for LAr Pumps | FSCF shall provide lifting eyelets grid (1 m X 1 m with each eyelet having a minimum capacity of 2 metric tons) in the crown of the caverns above the LAr pumps to aid LAr pumps installation/maintenance |  |  | Docdb-464
FSCF-Engr-129 | requirement |  | Peak particle velocity | FSCF shall ensure that the peak particle velocity during blasting and air over pressure, measured at nearest surface property boundary and nearest experiment underground, comply with the limits described in docdb-1655 |  |  | Docdb-1655
FSCF-Engr-147 | requirement | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross Cage Requirements | FSCF shall provide a cage for the Ross shaft for the transportation of personnel and components/equipment from the surface to the 4850 L
FSCF-Engr-130 | Specification/parameter | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross cage specifications | The Ross Cage shall have minimum internal clearance height of 3.6m (11’ 10”)
FSCF-Engr-131 | Specification/parameter | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross cage specifications | The Ross Cage doors shall be removable to allow full use of this height.
FSCF-Engr-132 | Specification/parameter | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross cage specifications | The Ross Cage shall have minimum internal clearance length between doors of 3.69m (12’ 1.5”)
FSCF-Engr-133 | Specification/parameter | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross cage specifications | The Ross Cage shall have minimum internal clearance width between any protrusions of 1.38m (4’ 6.25”)
FSCF-Engr-134 | Specification/parameter | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross cage specifications | The Ross Cage shall have minimum load capacity inside the cage of 5,450 kg (12,000 lb) at full speed
FSCF-Engr-135 | Specification/parameter | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross cage specifications | The Ross Cage shall have minimum slinging capacity beneath cage 5,900 kg (13,000 lb) at reduced speed
FSCF-Engr-136 | Specification/parameter | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross cage specifications | The Ross Cage shall have minimum of 6 connection points beneath the cage, one at each corner, on at the midpoint of each long side
FSCF-Engr-137 | Specification/parameter | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross cage specifications | The Ross Cage shall have maximum overall height to allow slinging components 7.6m (25 ft) beneath the cage
FSCF-Engr-138 | Specification/parameter | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross cage specifications | The Ross Cage shall have minimum designed travel speed 12.7 m/s (2,500 fpm)
FSCF-Engr-139 | Specification/parameter | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross cage specifications | The Ross Cage shall have a flat work deck above cage capable of supporting a minimum of 1000 kg (2,200 lb) on each side of the emergency stop system.
FSCF-Engr-140 | requirement | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross cage emergency stop requirement | The Ross Cage shall meet all code requirements for emergency stopping
FSCF-Engr-141 | requirement | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross cage chairing mechanism | The Ross Cage shall have a chairing mechanism compatible with existing systems
FSCF-Engr-142 | requirement | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross cage rails | The Ross Cage shall have embedded rail compatible with existing rail
FSCF-Engr-143 | requirement | FDmod-gen-029, Cryostat-049, Cryosys-034 | Ross cage portholes | The Ross Cage shall incorporate portholes to allow visual monitoring of slung loads from inside the cage.
FSCF-Engr-144 | assumption |  | Surface Facilities command center | This space would centralize all facilities system monitoring (existing SDSTA and new LBNF) in one space. Therefore there are no CF requirements for this space. | This is where systems like fire alarm and HVAC are monitored. SDSTA is seeking funding to create this space at the Yates complex, perhaps in the existing E&O building. | This is consistent with "addendum notes" from control room workshop, docdb-937 and Mike Headley's email from 7/7/2017
FSCF-Engr-145 | assumption |  | Surface experimental control room | This space would centralize all experiment monitoring (existing LZ and new DUNE) in one space, much like ROC at Fermilab. Therefore there are no CF requirements for this space. | This is where DUNE would be monitored. SDSTA is seeking funding to create this space at the Yates complex, perhaps in the existing E&O building. | This is consistent with "addendum notes" from control room workshop, docdb-937 and Mike Headley's email from 7/7/2017
FSCF-Engr-146 | requirement | Cryosys-082 | Bollards in CUC | FSCF shall provide removable type bollards in CUC with the in-ground sleeve flush with the floor finish surface to protect cryo equipment in CUC. | Additional requirements/specifications as per docdb-4751-v1
FSCF-Engr-148 | requirement | Cryostat-062, Cryosys-083 | Compressed air supply | FSCF shall provide supply of dry compressed air in the caverns at a pressure of 120 psig | This utility will be needed to operate the pneumatic valves, air powered tools, clean pieces after machining before installation, etc. | Number of outlets, max. delivery flow rate, total delivery flow rate is TBD
FSCF-Engr-149 | assumption |  | Primary access | Primary access through Ross shaft, no modification to existing east or west lab access drifts
FSCF-Engr-151 | Requirement | FDmod-gen-016 | Surface finish | FSCF shall provide all surface finishes as unpainted shotcrete. Floor of existing south access drifts and all new drifts will be concrete, except mucking ramps. All floor concrete is to be sealed. |  | Sealing needs to be defined
FSCF-Engr-153 | requirement | glo-prog-049, fs-prog-001 | Rock mass monitoring system | LBNF excavation design scope shall include design and cost estimation for installation of rock mass monitoring systems during construction through long-term operation including, but not limited to, blast vibration, piezometers, inclinometers, extensometers and convergence monitoring
FSCF-Engr-154 | requirement | Cryostat-064 | Cryostat loading | FSCF shall provide a concrete floor for seating the cryostat that will withstand the cryostat loading |  | The cryostat loading information is available in EDMS-1531410 v.1. All loading is in metric tonnes. Weblink: https://edms.cern.ch/ui/#!master/navigator/document?P:1472009535:1879028512:subDocs
FSCF-Engr-155 | requirement | cryostat-049, FDmod-gen-029, Cryosys-085 | Drift design and dimensions | FSCF shall construct all new drifts as recommended in the drift optimization study in docdb-1313 v2 |  |  | Docdb-1313
FSCF-Engr-156 | requirement |  | Ross shaft transportation and brow requirements | The Ross shaft and brow shall allow the transportation of loads as shown in DUNE docdbs-328, 4781, 4532 |  |  | Docdbs- 328, 4781, 4532
FSCF-Engr-157 | requirement |  | Access ways/Door ways | FSCF shall have doors with a minimum clearance when opened of 12' H X 8' 2.5" W according to docdb-136, UG-PDR-A-201 in all access ways from the Ross Shaft to the South, East and West passages to and between caverns |  |  | Docdb-136
FSCF-Engr-159 | requirement |  | Ross Shaft work decks and Yates Shaft cage use | The Ross Shaft work decks and the Yates Shaft cage shall be used in compliance with the constraints described in DUNE docdb-5786-v1 |  |  | Docdb-5786

## Revision History
ID | Type | Heading | Status/Change | Submitter | Author | Date
Docdb 112-version 10
FSCF-Engr-009 | Requirement | Central location for information through bulletin boards, online systems, monitors | Obsoleted (June 2017) | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-010 | Requirement | Central location for meetings | Obsoleted (June 2017) | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-013 | Requirement | Chamber slab on grade surface Tolerances | Updated text to reflect current understanding and added refernce docdb | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-014 | Requirement | Logistics plan | Updated heading, removed "surface". Added references. | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-031 | Requirement | DAQ computer systems and local data storage, network services | Obsoleted (June 2017) | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-032 | Requirement | DAQ control stations space | Obsoleted (June 2017) | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-057 | Requirement | Fire and life safety control station | Removed notes and reference docdb | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-068 | Requirement | LN2 Dewars space | Updated verbiage adding "approximately" for size of dewars. Also added notes regarding TBD size, shape and fit. | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-091 | Requirement | Surface control room | Added power required | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-098 | Requirement | Underground control room | Obsoleted (June 2017) | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-099 | Requirement | Underground control room cable trays and services | Obsoleted (June 2017) | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-100 | Requirement | Underground control room DAQ electronics racks | Obsoleted (June 2017) | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-102 | Requirement | Underground control room logbook storage space | Obsoleted (June 2017) | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-103 | Requirement | Underground control room space for calibration equipment | Obsoleted (June 2017) | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-104 | Requirement | Underground control room space for cryogenics control station | Obsoleted (June 2017) | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-105 | Requirement | Underground control room work spaces for visitors | Obsoleted (June 2017) | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-122 | Requirement | Components geometry and weight | Added new requirement | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-112 | Requirement | Clean room | Added parent | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-123 | requirement | Underground control room | Added new requirement | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-124 | requirement | Underground control room DAQ electronics racks | Added new requirement | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-125 | requirement | Underground control room space for cryogenics control station | Added new requirement | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-126 | requirement | Underground control room work spaces for visitors | Added new requirement | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-127 | requirement | Lifting eyelets for LAr Pumps | Added new requirement | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-071 | requirement | Mezzanine support | Added lifting eyes specifications | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-017 | requirement | Compressor Heat Exchangers - 1 (surface) | Added "surface" in heading | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-018 | requirement | Compressor Heat Exchangers - 2 (surface) | Added "surface" in heading | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-019 | requirement | Compressor Heat Exchangers - 3 (surface) | Added "surface" in heading | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-020 | requirement | Compressor Heat Exchangers - 4 (surface) | Added "surface" in heading | N. Dhanaraj |  | 2017-06-01
FSCF-Engr-027 | requirement | Cryogenics piping | The pipe sizes were updated | N. Dhanaraj |  | 2017-06-16
Docdb 112-version 11
FSCF-Engr-004 | requirement | Booster Compressor Cooling | Added correct parent and rationale and reference docdb | N. Dhanaraj |  | 2017-06-30
FSCF-Engr-006 | requirement | Cavern height | Rephrased requirement for clarity | N. Dhanaraj |  | 2017-06-30
FSCF-Engr-014 | requirement | Logistics Plan | Rephrased requirement | N. Dhanaraj |  | 2017-06-30
FSCF-Engr-130 to FSCF-Engr-139 | specification/parameter | Ross cage specifications | Added new specifications/parameters | N. Dhanaraj | J. Willhite | 2017-07-13
FSCF-Engr-091 | requirement | Surface control room | Obsoleted | N. Dhanaraj |  | 2017-07-13
FSCF-Engr-093 | requirement | Surface data transfer room | added 'transfer' to heading and rationale | N. Dhanaraj |  | 2017-07-13
FSCF-Engr-119 | requirement | Secondary containment | changed heading and added volume of oil | N. Dhanaraj | M. Adamowski | 2017-07-13
FSCF-Engr-123 | requirement | underground experimental work area | changed heading | N. Dhanaraj | E. James | 2017-07-13
FSCF-Engr-022 | requirement | Cryo building -1 | Need more info | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-028 | requirement | Cryogenics piping installation | Deleted, alread covered in design code | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-041 | Requirement | Far detector installation | Need more info | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-068 | Requirement | LN2 Dewars space | Need more info | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-081 | Requirement | Monorail longitudinal travel | Deleted, redundant | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-092 | Requirement | Surface cryogenics building piping penetrations | Deleted, redundant | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-107 | requirement | ventilation | Deleted, redundant | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-111 | requirement | wireless connectivity | Need more info | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-113 | requirement | chilled water supply | Deleted, redundant | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-115 | requirement | crane | Deleted, redundant | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-120 | requirement | Surface space for heat exchangers | deleted, FSCF scope | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-123 | requirement | Underground experimental work area | rephrased | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-124 | requirement | Underground data processing room | rephrased | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-125 | requirement | Underground cryogenics work area | rephrased | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-126 | requirement | Underground control room work space for visitors | Deleted, redundant | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-144 | assumption | Surface Facilities command center | Added new assumption | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-145 | assumption | Surface experimental control room | Added new assumption | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-128 | requirement | sealant on rock septum | Deleted, redundant | N. Dhanaraj |  | 2017-07-24
FSCF-Engr-146 | requirement | Bollards in CUC | Added new requirement | N. Dhanaraj |  | 2017-07-28
FSCF-Engr-147 | requirement | Ross cage requirements | Added new requirement | N. Dhanaraj |  | 2017-07-28
FSCF-Engr-140 | requirement | Ross cage emergency stop requirement | Added new requirement | N. Dhanaraj | J. Willhite | 2017-07-28
FSCF-Engr-141 | requirement | Ross cage chairing mechanism | Added new requirement | N. Dhanaraj | J. Willhite | 2017-07-28
FSCF-Engr-142 | requirement | Ross cage rails | Added new requirement | N. Dhanaraj | J. Willhite | 2017-07-28
FSCF-Engr-143 | requirement | Ross cage portholes | Added new requirement | N. Dhanaraj | J. Willhite | 2017-07-28
FSCF-Engr-148 | requirement | Compressed air supply | Added new requirement | N. Dhanaraj | D. Montanari | 2017-08-03
FSCF-Engr-005 | requirement | Cable fire rating | Added text on variance | N. Dhanaraj | M. Andrews | 2017-08-08
FSCF-Engr-012 | requirement | Central Utilities Cavern Space Allocation | Added DUNE data room to the text | N. Dhanaraj | J. Willhite | 2017-08-10
FSCF-Engr-027 | requirement | Cryogenics piping | Added notes | N. Dhanaraj | J. Willhite | 2017-08-10
FSCF-Engr-042 | Requirement | Fiber cable tray grounding | Added for "all" cable trays | N. Dhanaraj | J. Willhite | 2017-08-10
FSCF-Engr-123 | requirement | Underground experimental work area | Added phrase "within the underground control room" | N. Dhanaraj | J. Willhite | 2017-08-10
FSCF-Engr-125 | requirement | Underground cryogenics work area | Added phrase "within the underground control room" | N. Dhanaraj | J. Willhite | 2017-08-10
FSCF-Engr-124 | requirement | Underground data processing room | Added rationale on number of racks | N. Dhanaraj | J. Willhite | 2017-08-25
FSCF-Engr-149 | assumption | Primary access | Added new assumption | N. Dhanaraj | J. Willhite | 2017-10-03
FSCF-Engr-150 | assumption | Yates shaft | Added new assumption | N. Dhanaraj | J. Willhite | 2017-10-03
FSCF-Engr-151 | requirement | Surface finish | Added new requirement | N. Dhanaraj | T. Lundin | 2017-10-03
FSCF-Engr-152 | assumption | Low-radon concrete/shotcrete | Added new assumption | N. Dhanaraj | J. Willhite | 2017-10-03
FSCF-Engr-153 | requirement | Rock mass monitoring system | Added new requirement | N. Dhanaraj | T. Lundin | 2017-10-03
FSCF-Engr-154 | requirement | Cryostat loading | Added new requirement | N. Dhanaraj | T. Lundin | 2017-10-03
FSCF-Engr-155 | requirement | Drift design and dimensions | Added new requirement | N. Dhanaraj | T. Lundin | 2017-10-04
FSCF-Engr-156 | requirement | Ross shaft transportation and brow requirements | Added new requirement | N. Dhanaraj | J. Willhite | 2017-10-04
FSCF-Engr-157 | requirement | Access ways/Door ways | Added new requirement | N. Dhanaraj |  | 2017-10-04
FSCF-Engr-158 | requirement | Transportation of equipment with position specific limitations | Added new requirement | N. Dhanaraj |  | 2017-10-12
FSCF-Engr-159 | requirement | Ross Shaft work decks and Yates Shaft cage use | Added new requirement | N. Dhanaraj | J. Willhite | 2017-10-20