## Slide 1: LBNF/DUNE Cryogenics
David Montanari
LBNC Review
18-21 February 2018
Notes: Good afternoon ladies and gentlemen, I am going to give a brief introduction on the Long Baseline Neutrino Facility and its LAr and cryogenics needs.

## Slide 2: Thanks to
Mark Adamowski.
Johan Bremer.
Michel Chalifour.
Joaquim Creus Prats.
Marzio Nessi.
Stephen Pordes.
Notes: We have talked about the distinction between Fermilab (the Laboratory) and FRA (the legal entity).
Before we conclude, few words on FRA procurement and policies.
READ.

## Slide 3: Outline
LBNC Recommendation 2.1.
Agenda items.
DOR IPR Recommendations
Summary.
Notes: We have talked about the distinction between Fermilab (the Laboratory) and FRA (the legal entity).
Before we conclude, few words on FRA procurement and policies.
READ.

## Slide 4: LBNC Recommendation 2.1
R: Ensure that the cryogenics performance testing is given priority on ProtoDUNE and sufficient attention to collect data, baseline simulations, and iterate as needed.
A: We believe that we have adequately addressed the recommendation by providing:
  Detailed commissioning plan for the cryogenic system (as it will be performed by the manufacturer before delivery and after installation).
  Commissioning plan for the cryostat + cryogenics + detector inclusive of GAr purge, cool-down, filling, steady state operations (LAr purification, GAr boil-off recondensation and purification).
  DUNE has installed a comprehensive set of temperature monitors including two gradient monitors (one fixed and one movable) to measure the temperature inside the cryostat at the few mK level. This will help validate the CFD simulations of the motion of the LAr inside the cryostat.
Status: Closed (Feb 5, 2018).

## Slide 5: Agenda item 1
Q: Provide an update on the development of plans for pressure testing the far site cryostats.
A: Work in progress. Changes in LBNF Cryo-safety panel leadership.
  New leadership (Chair and Deputy) visited CERN end of Jan 2018 and met with CERN Neutrino Platform leadership and engineers.
  Looking at all documentation that was provided to understand the feasibility of the proposed test plan within the Lab ES&H policy.
  Goal is to prepare a risk analysis of the proposed test plan and make a determination soon.
  No further updates.

## Slide 6: Agenda item 2 – Intro
Q: Provide a plan for testing of cryogenics during the commissioning of ProtoDUNE as previously recommended.
A: Quality Plan from Demaco (manufacturer of the Proximity Cryogenics): https://edms.cern.ch/document/1900702/1. Highlights in next slides.
Specs:
  EN13445 & EN13480.
  PED (2014/68/EU).
  Design P: 10 bara.
  Design T: 77-300 K (all cryo but regen) and 500 K (regen).
Additional testing:
  Warm piping testing (Pressure test + He leak check).
  Controls test.
  Synchronization.

## Slide 7: Agenda item 2 – Highlights 1/2
Testing during fabrication (at Demaco):
  Welds (piping & vessels) Visual, X-ray, dye penetrant.
  Assembly  He leak check, Pressure test, Vacuum retention test.
  Instruments test  Valves, heaters, P/T sensors
  PSVs  Set pressure.
  Bellows  He leak check.
  Electrical breaks  Cold cycles, Pressure test, He leak check, electrical resistance (by CERN).
Final Inspection (at Demaco):
  Documentation.
  SEP statement.
  CE Declaration of Conformity.
  CE marking.
Factory Acceptance Test (at Demaco before shipping):
  Dimensional check.
  Pressure test.
  Helium leak check.
  PSVs pressure setting check.

## Slide 8: Agenda item 2 – Highlights 2/2
Testing during Installation (at CERN):
  Incoming inspection.
  Hydraulic continuity.
  Vacuum.
On Site Acceptance Test (Warm Acceptance Test):
  Purge & Flush system.
  Pressure Test.
  Helium leak check.
On Site Acceptance Test (Cold Acceptance Test):
  All interfaces installed and ready.
  Cold test with LN2.
  Helium leak check.

## Slide 9: DOE IPR Recommendation 9
R: Commit additional resources either within or interfacing with the cryogenic team to address areas such as system integration, controls and commissioning six to twelve months prior to CD-2.
A: We acknowledge the need to augment the staff to address areas that now require more attention, like cryogenics systems integration. We are working on a plan to identify these resources and add them in a timely fashion. LBNF/DUNE Integration is done at the Project Office level, with a group led by Jack F. One of them will be a designer shared with Systems Engineering.
Status: Open.

## Slide 10: DOE IPR Recommendation 10
R: Review and ensure all elements of the DOE scope are contained within the WBS (such as ODH system, cryogenic controls, system integration, commissioning of integrated system) by the next SOE/SC review.
A: The ODH system was identified as missing scope. We have prepared a map of ODH heads/control boxes, tabulated wiring and programming and included the resources needed for the implementation. Details in next slides. We will do a Change Request after DOE OPR (schedule is already frozen) to add it to RLS.
Status: Open (working towards resolution).

## Slide 11: DOE IPR Recommendation 10 – ODH Sensors/Control Boxes Above Ground and Ross Cage

## Slide 12: DOE IPR Recommendation 10 – ODH Sensors/Control Boxes Underground

## Slide 13: DOE IPR Recommendation 10 – ODH Info 1/2
Surface/Cavern productivity factors for working at SURF (from Jacobs).
Route complexity factors (from LBNF Cryo).
8 Man-hr to pull 50 feet of cable (from TD Cryo Sector).
16 Man-hr to install/program chassis (from TD Cryo Sector).
Derived:
  Surface/Cavern cable pulling factors.
  Surface/Cavern control boxes installation and programming factors.

## Slide 14: DOE IPR Recommendation 10 – ODH Info 2/2
$120k M&S
2,700 man-hr wiring (techs)
470 man-hr programming (Eng)

## Slide 15: Summary
We believe that we have addressed the review recommendations from the Oct-2017 LBNC meeting and provided an update of the activities covering the proposed agenda items.
We have a plan to address the recommendations from the 2017 DOE IPR.
Another contribution will present the current status of the LBNF Cryogenics.
Notes: We have talked about the distinction between Fermilab (the Laboratory) and FRA (the legal entity).
Before we conclude, few words on FRA procurement and policies.
READ.

## Slide 16: Thanks
Notes: We have talked about the distinction between Fermilab (the Laboratory) and FRA (the legal entity).
Before we conclude, few words on FRA procurement and policies.
READ.

## Slide 17: Backup
Notes: We have talked about the distinction between Fermilab (the Laboratory) and FRA (the legal entity).
Before we conclude, few words on FRA procurement and policies.
READ.

## Slide 18: Commissioning Plan (from DUNE Collaboration Meeting)
Notes: We have talked about the distinction between Fermilab (the Laboratory) and FRA (the legal entity).
Before we conclude, few words on FRA procurement and policies.
READ.