## Slide 1: Mu2E Septa Fluorinert (FC-40) Feedthrough Preliminary Flow Modeling
Abhishek Deshpande (Dez)
Update
March 12, 2018

## Slide 2: Overview
Geometry
  Inlet and outlet in the same plane (Horizontal inlet)
  Inlet and outlet in different planes (Vertical inlet)
Flow model details
Results
Geometry modified
  Fluid gap reduced to 0.5 In.
Velocity profiles for the modified geometry
Geometry modified
  An annular tube section is placed in the shell
  Velocity profiles in the inner shell section
Conclusions
Future work

## Slide 3: Geometry: Inlet and outlet in the same plane

## Slide 4: Geometry: Inlet and outlet in different planes

## Slide 5: Flow model details
ANSYS CFX was used to model the flow.
Transient simulation:
  Total time: 4 s.
  Time step: 0.01 s.
Turbulence model: k-epsilon.
Isothermal solids and fluids. 25 Deg.C.
Grid independent solution simulated.
FC-40 properties used.

## Slide 6: Results
Mid-plane vertical component velocity contour
Mid-plane vertical component velocity contour

## Slide 7: Results
Chart: Velocity profile at 1 IN. from the bottom of the FC-40 volume
| 1.30999994 | 1.28353524 | 1.2570706599999999 | 1.2306059600000001 | 1.2041412600000001 | 1.1776765600000001 | 1.15121198 | 1.12474728 | 1.09828258 | 1.07181799 | 1.04535329 | 1.01888859 | 0.992423952 | 0.96595925100000002 | 0.93949461000000001 | 0.91302990900000003 | 0.88656526800000002 | 0.86010062700000001 | 0.83363592600000003 | 0.80717128500000002 | 0.78070658400000004 | 0.75424194300000003 | 0.72777724300000002 | 0.70131260200000001 | 0.67484790100000003 | 0.64838326000000002 | 0.62191855900000004 | 0.59545397799999999 | 0.56898933600000001 | 0.542524695 | 0.51606005399999999 | 0.48959544300000002 | 0.46313080200000001 | 0.436666161 | 0.41020155000000003 | 0.38373690799999999
Velocity profile at 4 sec for top inlet | 0 | -0.43414 | -0.69203 | -0.70707 | -0.70849 | -0.70476 | -0.69309 | -0.68 | -0.66414 | -0.64672 | -0.62837 | -0.60888 | -0.58906 | -0.56695 | -0.54454 | -0.52148 | -0.49916 | -0.47758 | -0.45476 | -0.43121 | -0.4072 | -0.38239 | -0.35795 | -0.33396 | -0.31008 | -0.28669 | -0.26424 | -0.2425 | -0.22062 | -0.19992 | -0.18015 | -0.1614 | -0.14452 | -0.1283 | -0.11177 | 0
Velocity profile at 4 sec for side inlet | 0 | 0.11137 | 0.11652 | 0.12033 | 0.1237 | 0.12694 | 0.13022 | 0.13365 | 0.13738 | 0.14125 | 0.14518 | 0.14927 | 0.15368 | 0.15837 | 0.16325 | 0.16882 | 0.17443 | 0.18014 | 0.1859 | 0.19193 | 0.19845 | 0.20483 | 0.21104 | 0.21765 | 0.22467 | 0.23193 | 0.23917 | 0.24633 | 0.25332 | 0.25997 | 0.26644 | 0.27196 | 0.27674 | 0.27952 | 0.17772 | 0
Velocity profile at 4 sec for side inlet | 0 | -0.061108 | -0.096827 | -0.097573 | -0.096941 | -0.095776 | -0.093423 | -0.090757 | -0.087515 | -0.083814 | -0.079891 | -0.075513 | -0.071021 | -0.066383 | -0.062063 | -0.058014 | -0.053716 | -0.049048 | -0.044733 | -0.040188 | -0.035466 | -0.030809 | -0.026303 | -0.022077 | -0.018234 | -0.014365 | -0.010443 | -0.0067498 | -0.0032488 | -9.1877e-05 | 0.0027527 | 0.0052998 | 0.0075497 | 0.0095993 | 0.011152 | 0
 | 0 | 0.039033 | 0.039377 | 0.03934 | 0.03905 | 0.038504 | 0.037945 | 0.037313 | 0.036564 | 0.035801 | 0.034937 | 0.034074 | 0.033132 | 0.032186 | 0.031181 | 0.030154 | 0.029129 | 0.028133 | 0.027184 | 0.026248 | 0.025082 | 0.023935 | 0.022854 | 0.021834 | 0.020824 | 0.019877 | 0.018956 | 0.018059 | 0.017182 | 0.016405 | 0.015676 | 0.015082 | 0.014523 | 0.014047 | 0.0087665 | 0

## Slide 8: Results: Animation (Hover over and click play)

## Slide 9: Results: Animation (Hover over and click play)

## Slide 10: Results: Animation (Hover over and click play)

## Slide 11: Modified design
Following design changes were made to the geometry:
A transient simulation was generated with a total time of 40 Sec.

## Slide 12: Velocity profiles
Chart: FC-40 velocity profiles in the shell region. Flow rate: 1 Gpm (1.34 m/s) through inlet
| -0.880000055 | -0.87115585799999995 | -0.86231166100000001 | -0.85346746399999995 | -0.84462326799999998 | -0.83577907100000004 | -0.82693487399999999 | -0.81809067700000004 | -0.80924647999999999 | -0.80040228400000002 | -0.79155808699999997 | -0.78271394999999999 | -0.77386975300000005 | -0.765025556 | -0.75618135900000005 | -0.747337162 | -0.73849296600000003 | -0.72964876899999997 | -0.72080457200000003 | -0.71196037499999998 | -0.70311617900000001 | -0.69427204099999995 | -0.68542784499999998 | -0.67658364800000004 | -0.66773945099999998 | -0.65889525400000004 | -0.65005105699999999 | -0.64120686100000002 | -0.63236266399999996 | -0.62351846700000002 | -0.61467426999999997 | -0.60583001400000003 | -0.59698581699999997 | -0.58814156100000003 | -0.57929736399999998 | -0.57045310699999996 | -0.56160891099999999 | -0.55276465399999997 | -0.54392045700000002 | -0.53507620099999997 | -0.52623200400000003 | -0.51738774799999998 | -0.50854355100000004 | -0.49969929499999999 | -0.49085506800000001 | -0.48201084100000002 | -0.47316661500000001 | -0.46432238799999997 | -0.45547816200000002 | -0.44663393499999998 | -0.437789708 | -0.42894548199999999 | -0.42010125500000001 | -0.411257029 | -0.40241280200000001 | -0.39356854600000002 | -0.38472431899999998 | -0.375880092 | -0.36703586599999999
Velocity profile at 1 sec. | 0 | 0 | -0.0073704 | -0.015652 | -0.023246 | -0.022939 | -0.022631 | -0.022324 | -0.021827 | -0.021266 | -0.020705 | -0.020145 | -0.019426 | -0.018696 | -0.017967 | -0.017156 | -0.016368 | -0.015463 | -0.014564 | -0.01367 | -0.012781 | -0.011898 | -0.011145 | -0.010181 | -0.009217 | -0.0082529 | -0.0072887 | -0.0063246 | -0.0053604 | -0.0043478 | -0.0032269 | -0.002106 | -0.00098506 | 0.00013584 | 0.0012418 | 0.0023404 | 0.003439 | 0.0045376 | 0.0056361 | 0.0067347 | 0.0079195 | 0.0091544 | 0.010366 | 0.011486 | 0.012838 | 0.014259 | 0.015682 | 0.017105 | 0.018411 | 0.019693 | 0.020975 | 0.022076 | 0.023072 | 0.02405 | 0.024602 | 0.025153 | 0.0119 | 0 | 0
 | 0 | 0 | -0.0017418 | -0.0042387 | -0.0039635 | -0.0036117 | -0.0031246 | -0.0026158 | -0.0020838 | -0.0014957 | -0.00090752 | -0.0003165 | 0.00029263 | 0.00090181 | 0.0015109 | 0.0020831 | 0.0025172 | 0.002886 | 0.0032157 | 0.0035454 | 0.0038751 | 0.0042049 | 0.004529 | 0.0048495 | 0.00517 | 0.0054905 | 0.005811 | 0.0060057 | 0.0061227 | 0.0062457 | 0.0064566 | 0.0066675 | 0.0068783 | 0.0070892 | 0.0073001 | 0.0075109 | 0.0077218 | 0.0079632 | 0.0080723 | 0.0081531 | 0.0082333 | 0.0083128 | 0.0083916 | 0.0084627 | 0.008546 | 0.0086006 | 0.0086548 | 0.0087147 | 0.0088024 | 0.0088906 | 0.0089788 | 0.0090711 | 0.00919 | 0.0093092 | 0.0094287 | 0.0064889 | 0.0030669 | 0 | 0
Velocity profile at 10 sec. | 0 | 0 | -0.0052399 | -0.011132 | -0.016598 | -0.017099 | -0.017601 | -0.018103 | -0.018593 | -0.019078 | -0.019563 | -0.020049 | -0.020474 | -0.020896 | -0.021317 | -0.021708 | -0.022091 | -0.022375 | -0.02266 | -0.022946 | -0.023233 | -0.02352 | -0.023623 | -0.023664 | -0.023705 | -0.023746 | -0.023786 | -0.023827 | -0.023868 | -0.023846 | -0.023683 | -0.02352 | -0.023357 | -0.023195 | -0.022968 | -0.022709 | -0.02245 | -0.022192 | -0.021933 | -0.021674 | -0.021355 | -0.021 | -0.02062 | -0.020138 | -0.019639 | -0.019135 | -0.018631 | -0.018128 | -0.017583 | -0.017029 | -0.016475 | -0.01592 | -0.015364 | -0.014811 | -0.014304 | -0.013798 | -0.0064962 | 0 | 0
 | 0 | 0 | 0.011295 | 0.027486 | 0.028101 | 0.028286 | 0.028388 | 0.028476 | 0.02855 | 0.028588 | 0.028626 | 0.028661 | 0.028681 | 0.028701 | 0.02872 | 0.028744 | 0.028779 | 0.028815 | 0.028852 | 0.028888 | 0.028924 | 0.02896 | 0.029004 | 0.029052 | 0.0291 | 0.029148 | 0.029197 | 0.029255 | 0.029319 | 0.02937 | 0.029232 | 0.029093 | 0.028954 | 0.028815 | 0.028676 | 0.028537 | 0.028399 | 0.028259 | 0.028183 | 0.02812 | 0.028056 | 0.027993 | 0.027929 | 0.027847 | 0.02773 | 0.027636 | 0.027542 | 0.027443 | 0.02729 | 0.027135 | 0.02698 | 0.026815 | 0.026579 | 0.026343 | 0.026109 | 0.017919 | 0.0084712 | 0 | 0
Velocity profile at 20 sec. | 0 | 0 | -0.014364 | -0.030502 | -0.045393 | -0.045954 | -0.046514 | -0.047075 | -0.047428 | -0.047711 | -0.047994 | -0.048277 | -0.04834 | -0.048315 | -0.04829 | -0.048389 | -0.048343 | -0.04809 | -0.047838 | -0.047586 | -0.047336 | -0.047087 | -0.046264 | -0.045515 | -0.044765 | -0.044015 | -0.043266 | -0.042516 | -0.041766 | -0.041092 | -0.040587 | -0.040082 | -0.039577 | -0.039073 | -0.038229 | -0.037218 | -0.036207 | -0.035196 | -0.034185 | -0.033175 | -0.032248 | -0.031371 | -0.030484 | -0.029557 | -0.028577 | -0.027582 | -0.026588 | -0.025596 | -0.024648 | -0.023709 | -0.022771 | -0.021883 | -0.021023 | -0.020168 | -0.0194 | -0.018631 | -0.0087682 | 0 | 0
 | 0 | 0 | 0.011587 | 0.028198 | 0.028872 | 0.029107 | 0.029234 | 0.029344 | 0.029425 | 0.029433 | 0.029442 | 0.02944 | 0.029364 | 0.029288 | 0.029211 | 0.029126 | 0.029007 | 0.028833 | 0.028626 | 0.028418 | 0.028211 | 0.028004 | 0.027788 | 0.027567 | 0.027346 | 0.027126 | 0.026905 | 0.026624 | 0.026307 | 0.025991 | 0.025699 | 0.025407 | 0.025115 | 0.024823 | 0.024531 | 0.024239 | 0.023947 | 0.023698 | 0.023403 | 0.023097 | 0.022791 | 0.022484 | 0.022178 | 0.021877 | 0.021548 | 0.021271 | 0.020993 | 0.020707 | 0.020444 | 0.020182 | 0.01992 | 0.01966 | 0.019411 | 0.019163 | 0.018916 | 0.012974 | 0.0061329 | 0 | 0
Velocity profile at 30 sec. | 0 | 0 | -0.0040005 | -0.0084925 | -0.012645 | -0.012925 | -0.013205 | -0.013485 | -0.01374 | -0.013985 | -0.014231 | -0.014477 | -0.014672 | -0.014815 | -0.014957 | -0.015305 | -0.0155 | -0.015649 | -0.015796 | -0.015939 | -0.01608 | -0.016217 | -0.016106 | -0.016154 | -0.016201 | -0.016249 | -0.016296 | -0.016344 | -0.016391 | -0.016471 | -0.016621 | -0.016771 | -0.016921 | -0.017072 | -0.017075 | -0.017007 | -0.016939 | -0.01687 | -0.016802 | -0.016734 | -0.016773 | -0.016875 | -0.016973 | -0.017053 | -0.017098 | -0.017132 | -0.017167 | -0.017201 | -0.017201 | -0.017193 | -0.017185 | -0.017122 | -0.017027 | -0.016927 | -0.016723 | -0.01652 | -0.0077932 | 0 | 0
 | 0 | 0 | 0.0074285 | 0.018077 | 0.018542 | 0.018726 | 0.018834 | 0.018933 | 0.019011 | 0.019042 | 0.019074 | 0.019099 | 0.019084 | 0.019069 | 0.019054 | 0.019032 | 0.018984 | 0.01891 | 0.01882 | 0.01873 | 0.018639 | 0.018549 | 0.01848 | 0.018425 | 0.018369 | 0.018314 | 0.018258 | 0.018176 | 0.018076 | 0.017981 | 0.01794 | 0.017898 | 0.017857 | 0.017815 | 0.017774 | 0.017732 | 0.017691 | 0.01769 | 0.017708 | 0.017728 | 0.017747 | 0.017765 | 0.017783 | 0.01781 | 0.017781 | 0.017845 | 0.017908 | 0.017954 | 0.017988 | 0.018021 | 0.018054 | 0.018079 | 0.018049 | 0.018019 | 0.017989 | 0.01236 | 0.0058443 | 0 | 0
Velocity profile at 40 sec. | 0 | 0 | 0.00077853 | 0.0016529 | 0.0024687 | 0.0026131 | 0.0027576 | 0.0029021 | 0.0030908 | 0.0032946 | 0.0034986 | 0.0037028 | 0.0039425 | 0.0041826 | 0.0044221 | 0.0046912 | 0.004946 | 0.0052168 | 0.005488 | 0.0057596 | 0.0060317 | 0.0063043 | 0.0066075 | 0.0068931 | 0.0071786 | 0.0074642 | 0.0077497 | 0.0080353 | 0.0083208 | 0.0085899 | 0.0088224 | 0.0090548 | 0.0092873 | 0.0095197 | 0.0097504 | 0.0099801 | 0.01021 | 0.01044 | 0.010669 | 0.010899 | 0.011103 | 0.011292 | 0.011479 | 0.011658 | 0.011794 | 0.011918 | 0.012041 | 0.012164 | 0.012245 | 0.012317 | 0.012389 | 0.01243 | 0.012452 | 0.012473 | 0.012443 | 0.012414 | 0.0058614 | 0 | 0
 | 0 | 0 | 0.0046091 | 0.011216 | 0.011284 | 0.011171 | 0.010936 | 0.010681 | 0.010386 | 0.0099941 | 0.0096021 | 0.0091934 | 0.0086741 | 0.0081542 | 0.0076341 | 0.007091 | 0.0064626 | 0.0058398 | 0.0052204 | 0.0046009 | 0.0039815 | 0.0033621 | 0.0027261 | 0.0020796 | 0.0014331 | 0.0007866 | 0.0001401 | -0.00060531 | -0.0014118 | -0.0022157 | -0.0029805 | -0.0037453 | -0.0045101 | -0.0052749 | -0.0060397 | -0.0068045 | -0.0075693 | -0.008324 | -0.0091974 | -0.010094 | -0.010988 | -0.011881 | -0.012773 | -0.013599 | -0.014361 | -0.015118 | -0.015875 | -0.016628 | -0.017176 | -0.017719 | -0.018261 | -0.018764 | -0.01902 | -0.019275 | -0.019531 | -0.013445 | -0.0063567 | 0 | 0

## Slide 13: Velocity profiles
Chart: FC-40 velocity profiles in the shell region. Flow rate: 2 Gpm (2.68 m/s) through inlet
| -0.880000055 | -0.87115585799999995 | -0.86231166100000001 | -0.85346746399999995 | -0.84462326799999998 | -0.83577907100000004 | -0.82693487399999999 | -0.81809067700000004 | -0.80924647999999999 | -0.80040228400000002 | -0.79155808699999997 | -0.78271394999999999 | -0.77386975300000005 | -0.765025556 | -0.75618135900000005 | -0.747337162 | -0.73849296600000003 | -0.72964876899999997 | -0.72080457200000003 | -0.71196037499999998 | -0.70311617900000001 | -0.69427204099999995 | -0.68542784499999998 | -0.67658364800000004 | -0.66773945099999998 | -0.65889525400000004 | -0.65005105699999999 | -0.64120686100000002 | -0.63236266399999996 | -0.62351846700000002 | -0.61467426999999997 | -0.60583001400000003 | -0.59698581699999997 | -0.58814156100000003 | -0.57929736399999998 | -0.57045310699999996 | -0.56160891099999999 | -0.55276465399999997 | -0.54392045700000002 | -0.53507620099999997 | -0.52623200400000003 | -0.51738774799999998 | -0.50854355100000004 | -0.49969929499999999 | -0.49085506800000001 | -0.48201084100000002 | -0.47316661500000001 | -0.46432238799999997 | -0.45547816200000002 | -0.44663393499999998 | -0.437789708 | -0.42894548199999999 | -0.42010125500000001 | -0.411257029 | -0.40241280200000001 | -0.39356854600000002 | -0.38472431899999998 | -0.375880092 | -0.36703586599999999
Velocity profile at 1 sec | 0 | 0 | 0.011567 | 0.024561 | 0.036496 | 0.036262 | 0.036028 | 0.035794 | 0.035274 | 0.034656 | 0.034037 | 0.033419 | 0.032565 | 0.031647 | 0.030729 | 0.029853 | 0.02892 | 0.027899 | 0.026877 | 0.025852 | 0.024825 | 0.023796 | 0.022706 | 0.021633 | 0.02056 | 0.019486 | 0.018413 | 0.01734 | 0.016267 | 0.015231 | 0.014279 | 0.013327 | 0.012376 | 0.011424 | 0.010429 | 0.009413 | 0.0083967 | 0.0073805 | 0.0063643 | 0.005348 | 0.0043993 | 0.0034899 | 0.0025992 | 0.0017839 | 0.00098819 | 0.00019853 | -0.00059085 | -0.0013799 | -0.0020033 | -0.0025906 | -0.0031777 | -0.0036314 | -0.0040074 | -0.004375 | -0.0045508 | -0.0047266 | -0.0022392 | 0 | 0
 | 0 | 0 | -0.010387 | -0.025274 | -0.025591 | -0.025505 | -0.025261 | -0.024993 | -0.024695 | -0.024324 | -0.023955 | -0.023581 | -0.023175 | -0.022771 | -0.022367 | -0.021981 | -0.021655 | -0.02118 | -0.020616 | -0.020052 | -0.019488 | -0.018924 | -0.018382 | -0.017853 | -0.017325 | -0.016796 | -0.016268 | -0.015819 | -0.015418 | -0.015021 | -0.014676 | -0.014331 | -0.013986 | -0.013641 | -0.013296 | -0.012952 | -0.012607 | -0.012284 | -0.012038 | -0.011803 | -0.011564 | -0.01132 | -0.011072 | -0.010839 | -0.01061 | -0.010391 | -0.010172 | -0.0099465 | -0.0097289 | -0.0095114 | -0.0092937 | -0.0090739 | -0.0088416 | -0.0086098 | -0.0083783 | -0.0057346 | -0.0027105 | 0 | 0
Velocity profile at 10 sec | 0 | 0 | -0.0018153 | -0.0038523 | -0.0056814 | -0.0051483 | -0.004615 | -0.0040816 | -0.0033097 | -0.0024566 | -0.0016035 | -0.00075032 | 0.00028105 | 0.0013351 | 0.0023887 | 0.00351 | 0.0045862 | 0.0056672 | 0.0067463 | 0.0078235 | 0.0088988 | 0.0099721 | 0.010834 | 0.011757 | 0.012681 | 0.013604 | 0.014528 | 0.015451 | 0.016375 | 0.017286 | 0.01817 | 0.019053 | 0.019937 | 0.020821 | 0.021511 | 0.022107 | 0.022703 | 0.023299 | 0.023895 | 0.024491 | 0.025088 | 0.025685 | 0.026241 | 0.026631 | 0.026782 | 0.026862 | 0.026942 | 0.027022 | 0.026962 | 0.026871 | 0.02678 | 0.02662 | 0.026422 | 0.026221 | 0.025961 | 0.025701 | 0.012127 | 0 | 0
 | 0 | 0 | 0.0091472 | 0.02226 | 0.022466 | 0.022315 | 0.021945 | 0.02154 | 0.021069 | 0.020441 | 0.019812 | 0.019163 | 0.018381 | 0.017598 | 0.016816 | 0.016046 | 0.015326 | 0.014584 | 0.013829 | 0.013074 | 0.012319 | 0.011564 | 0.01079 | 0.010003 | 0.0092166 | 0.00843 | 0.0076435 | 0.0067358 | 0.0057534 | 0.0047836 | 0.0039985 | 0.0032134 | 0.0024283 | 0.0016432 | 0.00085815 | 7.3056e-05 | -0.00071204 | -0.0014819 | -0.0025137 | -0.0035957 | -0.0046749 | -0.0057514 | -0.0068251 | -0.0078495 | -0.0088238 | -0.0097954 | -0.010768 | -0.011736 | -0.012533 | -0.013324 | -0.014115 | -0.014863 | -0.015343 | -0.015823 | -0.016302 | -0.011249 | -0.0053185 | 0 | 0
Velocity profile at 20 sec | 0 | 0 | -0.011043 | -0.023449 | -0.034813 | -0.034214 | -0.033615 | -0.033015 | -0.031968 | -0.030769 | -0.029568 | -0.028367 | -0.026828 | -0.025218 | -0.023608 | -0.021982 | -0.020316 | -0.018496 | -0.016674 | -0.014851 | -0.013025 | -0.011198 | -0.0098872 | -0.0086626 | -0.007438 | -0.0062133 | -0.0049887 | -0.0037641 | -0.0025395 | -0.0013021 | -3.624e-05 | 0.0012296 | 0.0024955 | 0.0037613 | 0.0048212 | 0.0057797 | 0.0067382 | 0.0076967 | 0.0086552 | 0.0096136 | 0.010552 | 0.01148 | 0.012396 | 0.013265 | 0.013879 | 0.014416 | 0.014953 | 0.01549 | 0.015818 | 0.0161 | 0.016382 | 0.016535 | 0.016612 | 0.016684 | 0.016621 | 0.016559 | 0.0078168 | 0 | 0
 | 0 | 0 | 0.0085194 | 0.020732 | 0.021 | 0.020938 | 0.020709 | 0.020453 | 0.020144 | 0.019708 | 0.019271 | 0.018816 | 0.018227 | 0.017639 | 0.01705 | 0.016442 | 0.01576 | 0.015057 | 0.014343 | 0.013628 | 0.012913 | 0.012198 | 0.011452 | 0.010687 | 0.0099219 | 0.0091566 | 0.0083913 | 0.0074794 | 0.0064769 | 0.0054846 | 0.0046413 | 0.0037979 | 0.0029546 | 0.0021113 | 0.001268 | 0.00042468 | -0.00041864 | -0.0012665 | -0.0022731 | -0.0033069 | -0.0043367 | -0.0053622 | -0.0063835 | -0.0073364 | -0.0081952 | -0.0090854 | -0.0099772 | -0.010857 | -0.01153 | -0.012198 | -0.012864 | -0.013489 | -0.013855 | -0.014221 | -0.014586 | -0.010059 | -0.0047566 | 0 | 0
Velocity profile at 30 sec | 0 | 0 | -0.0047319 | -0.010051 | -0.014925 | -0.014657 | -0.01439 | -0.014123 | -0.013546 | -0.012863 | -0.01218 | -0.011495 | -0.010577 | -0.0096208 | -0.0086645 | -0.0076688 | -0.0066701 | -0.0055872 | -0.0045004 | -0.0034096 | -0.0023149 | -0.0012162 | -0.00043404 | 0.00030129 | 0.0010366 | 0.0017719 | 0.0025073 | 0.0032426 | 0.0039779 | 0.0047385 | 0.0055554 | 0.0063723 | 0.0071892 | 0.0080062 | 0.0086974 | 0.0093267 | 0.009956 | 0.010585 | 0.011215 | 0.011844 | 0.012477 | 0.013113 | 0.013771 | 0.014517 | 0.015037 | 0.01549 | 0.015942 | 0.016395 | 0.016693 | 0.016957 | 0.017222 | 0.017378 | 0.017471 | 0.017559 | 0.017507 | 0.017455 | 0.0082406 | 0 | 0
 | 0 | 0 | 0.0049171 | 0.011966 | 0.011842 | 0.011521 | 0.010922 | 0.010279 | 0.0095477 | 0.0086058 | 0.0076634 | 0.0066933 | 0.0055408 | 0.0043873 | 0.0032332 | 0.0020846 | 0.00095879 | -0.00014434 | -0.0012339 | -0.0023234 | -0.003413 | -0.0045025 | -0.0056548 | -0.0068472 | -0.0080397 | -0.0092321 | -0.010425 | -0.011661 | -0.012926 | -0.014183 | -0.015339 | -0.016496 | -0.017653 | -0.018809 | -0.019966 | -0.021122 | -0.022279 | -0.02343 | -0.024639 | -0.025856 | -0.027069 | -0.028279 | -0.029483 | -0.030424 | -0.031044 | -0.031739 | -0.032436 | -0.033114 | -0.033296 | -0.033464 | -0.033633 | -0.033737 | -0.033446 | -0.033155 | -0.032864 | -0.022557 | -0.010665 | 0 | 0
Velocity profile at 40 sec | 0 | 0 | 0.0023298 | 0.0049464 | 0.007379 | 0.0077064 | 0.0080337 | 0.0083609 | 0.008805 | 0.0092889 | 0.0097724 | 0.010256 | 0.010815 | 0.011369 | 0.011921 | 0.012552 | 0.013129 | 0.013701 | 0.014273 | 0.014844 | 0.015414 | 0.015984 | 0.016518 | 0.017094 | 0.01767 | 0.018246 | 0.018822 | 0.019398 | 0.019974 | 0.020512 | 0.020966 | 0.021419 | 0.021872 | 0.022325 | 0.022736 | 0.023126 | 0.023516 | 0.023907 | 0.024297 | 0.024687 | 0.025111 | 0.025554 | 0.025975 | 0.026312 | 0.026566 | 0.026795 | 0.027025 | 0.027254 | 0.027382 | 0.027488 | 0.027594 | 0.027618 | 0.027593 | 0.027562 | 0.027406 | 0.027249 | 0.012862 | 0 | 0
 | 0 | 0 | 0.0071877 | 0.017491 | 0.017525 | 0.017275 | 0.016772 | 0.016229 | 0.015609 | 0.014804 | 0.013999 | 0.013165 | 0.012141 | 0.011117 | 0.010092 | 0.0090564 | 0.007984 | 0.0069333 | 0.0058956 | 0.0048579 | 0.0038202 | 0.0027826 | 0.0016918 | 0.00056701 | -0.00055774 | -0.0016825 | -0.0028072 | -0.0040168 | -0.0052787 | -0.0065304 | -0.0076323 | -0.0087343 | -0.0098363 | -0.010938 | -0.01204 | -0.013142 | -0.014244 | -0.015418 | -0.01676 | -0.01813 | -0.019497 | -0.020862 | -0.022225 | -0.023439 | -0.02448 | -0.025559 | -0.026639 | -0.027712 | -0.028286 | -0.028848 | -0.02941 | -0.029897 | -0.029919 | -0.029942 | -0.029966 | -0.020593 | -0.0097357 | 0 | 0

## Slide 14: Velocity profiles
Chart: FC-40 velocity profiles in the shell region. Flow rate: 1 Gpm (1.34 m/s) through the inlet.
| -0.880000055 | -0.87115585799999995 | -0.86231166100000001 | -0.85346746399999995 | -0.84462326799999998 | -0.83577907100000004 | -0.82693487399999999 | -0.81809067700000004 | -0.80924647999999999 | -0.80040228400000002 | -0.79155808699999997 | -0.78271394999999999 | -0.77386975300000005 | -0.765025556 | -0.75618135900000005 | -0.747337162 | -0.73849296600000003 | -0.72964876899999997 | -0.72080457200000003 | -0.71196037499999998 | -0.70311617900000001 | -0.69427204099999995 | -0.68542784499999998 | -0.67658364800000004 | -0.66773945099999998 | -0.65889525400000004 | -0.65005105699999999 | -0.64120686100000002 | -0.63236266399999996 | -0.62351846700000002 | -0.61467426999999997 | -0.60583001400000003 | -0.59698581699999997 | -0.58814156100000003 | -0.57929736399999998 | -0.57045310699999996 | -0.56160891099999999 | -0.55276465399999997 | -0.54392045700000002 | -0.53507620099999997 | -0.52623200400000003 | -0.51738774799999998 | -0.50854355100000004 | -0.49969929499999999 | -0.49085506800000001 | -0.48201084100000002 | -0.47316661500000001 | -0.46432238799999997 | -0.45547816200000002 | -0.44663393499999998 | -0.437789708 | -0.42894548199999999 | -0.42010125500000001 | -0.411257029 | -0.40241280200000001 | -0.39356854600000002 | -0.38472431899999998 | -0.375880092 | -0.36703586599999999
Velocity profile at 1 sec. | 0 | 0 | -0.0073704 | -0.015652 | -0.023246 | -0.022939 | -0.022631 | -0.022324 | -0.021827 | -0.021266 | -0.020705 | -0.020145 | -0.019426 | -0.018696 | -0.017967 | -0.017156 | -0.016368 | -0.015463 | -0.014564 | -0.01367 | -0.012781 | -0.011898 | -0.011145 | -0.010181 | -0.009217 | -0.0082529 | -0.0072887 | -0.0063246 | -0.0053604 | -0.0043478 | -0.0032269 | -0.002106 | -0.00098506 | 0.00013584 | 0.0012418 | 0.0023404 | 0.003439 | 0.0045376 | 0.0056361 | 0.0067347 | 0.0079195 | 0.0091544 | 0.010366 | 0.011486 | 0.012838 | 0.014259 | 0.015682 | 0.017105 | 0.018411 | 0.019693 | 0.020975 | 0.022076 | 0.023072 | 0.02405 | 0.024602 | 0.025153 | 0.0119 | 0 | 0
 | 0 | 0 | -0.0017418 | -0.0042387 | -0.0039635 | -0.0036117 | -0.0031246 | -0.0026158 | -0.0020838 | -0.0014957 | -0.00090752 | -0.0003165 | 0.00029263 | 0.00090181 | 0.0015109 | 0.0020831 | 0.0025172 | 0.002886 | 0.0032157 | 0.0035454 | 0.0038751 | 0.0042049 | 0.004529 | 0.0048495 | 0.00517 | 0.0054905 | 0.005811 | 0.0060057 | 0.0061227 | 0.0062457 | 0.0064566 | 0.0066675 | 0.0068783 | 0.0070892 | 0.0073001 | 0.0075109 | 0.0077218 | 0.0079632 | 0.0080723 | 0.0081531 | 0.0082333 | 0.0083128 | 0.0083916 | 0.0084627 | 0.008546 | 0.0086006 | 0.0086548 | 0.0087147 | 0.0088024 | 0.0088906 | 0.0089788 | 0.0090711 | 0.00919 | 0.0093092 | 0.0094287 | 0.0064889 | 0.0030669 | 0 | 0
Velocity profile at 10 sec. | 0 | 0 | -0.0052399 | -0.011132 | -0.016598 | -0.017099 | -0.017601 | -0.018103 | -0.018593 | -0.019078 | -0.019563 | -0.020049 | -0.020474 | -0.020896 | -0.021317 | -0.021708 | -0.022091 | -0.022375 | -0.02266 | -0.022946 | -0.023233 | -0.02352 | -0.023623 | -0.023664 | -0.023705 | -0.023746 | -0.023786 | -0.023827 | -0.023868 | -0.023846 | -0.023683 | -0.02352 | -0.023357 | -0.023195 | -0.022968 | -0.022709 | -0.02245 | -0.022192 | -0.021933 | -0.021674 | -0.021355 | -0.021 | -0.02062 | -0.020138 | -0.019639 | -0.019135 | -0.018631 | -0.018128 | -0.017583 | -0.017029 | -0.016475 | -0.01592 | -0.015364 | -0.014811 | -0.014304 | -0.013798 | -0.0064962 | 0 | 0
 | 0 | 0 | 0.011295 | 0.027486 | 0.028101 | 0.028286 | 0.028388 | 0.028476 | 0.02855 | 0.028588 | 0.028626 | 0.028661 | 0.028681 | 0.028701 | 0.02872 | 0.028744 | 0.028779 | 0.028815 | 0.028852 | 0.028888 | 0.028924 | 0.02896 | 0.029004 | 0.029052 | 0.0291 | 0.029148 | 0.029197 | 0.029255 | 0.029319 | 0.02937 | 0.029232 | 0.029093 | 0.028954 | 0.028815 | 0.028676 | 0.028537 | 0.028399 | 0.028259 | 0.028183 | 0.02812 | 0.028056 | 0.027993 | 0.027929 | 0.027847 | 0.02773 | 0.027636 | 0.027542 | 0.027443 | 0.02729 | 0.027135 | 0.02698 | 0.026815 | 0.026579 | 0.026343 | 0.026109 | 0.017919 | 0.0084712 | 0 | 0
Velocity profile at 20 sec. | 0 | 0 | -0.014364 | -0.030502 | -0.045393 | -0.045954 | -0.046514 | -0.047075 | -0.047428 | -0.047711 | -0.047994 | -0.048277 | -0.04834 | -0.048315 | -0.04829 | -0.048389 | -0.048343 | -0.04809 | -0.047838 | -0.047586 | -0.047336 | -0.047087 | -0.046264 | -0.045515 | -0.044765 | -0.044015 | -0.043266 | -0.042516 | -0.041766 | -0.041092 | -0.040587 | -0.040082 | -0.039577 | -0.039073 | -0.038229 | -0.037218 | -0.036207 | -0.035196 | -0.034185 | -0.033175 | -0.032248 | -0.031371 | -0.030484 | -0.029557 | -0.028577 | -0.027582 | -0.026588 | -0.025596 | -0.024648 | -0.023709 | -0.022771 | -0.021883 | -0.021023 | -0.020168 | -0.0194 | -0.018631 | -0.0087682 | 0 | 0
 | 0 | 0 | 0.011587 | 0.028198 | 0.028872 | 0.029107 | 0.029234 | 0.029344 | 0.029425 | 0.029433 | 0.029442 | 0.02944 | 0.029364 | 0.029288 | 0.029211 | 0.029126 | 0.029007 | 0.028833 | 0.028626 | 0.028418 | 0.028211 | 0.028004 | 0.027788 | 0.027567 | 0.027346 | 0.027126 | 0.026905 | 0.026624 | 0.026307 | 0.025991 | 0.025699 | 0.025407 | 0.025115 | 0.024823 | 0.024531 | 0.024239 | 0.023947 | 0.023698 | 0.023403 | 0.023097 | 0.022791 | 0.022484 | 0.022178 | 0.021877 | 0.021548 | 0.021271 | 0.020993 | 0.020707 | 0.020444 | 0.020182 | 0.01992 | 0.01966 | 0.019411 | 0.019163 | 0.018916 | 0.012974 | 0.0061329 | 0 | 0
Velocity profile at 30 sec. | 0 | 0 | -0.0040005 | -0.0084925 | -0.012645 | -0.012925 | -0.013205 | -0.013485 | -0.01374 | -0.013985 | -0.014231 | -0.014477 | -0.014672 | -0.014815 | -0.014957 | -0.015305 | -0.0155 | -0.015649 | -0.015796 | -0.015939 | -0.01608 | -0.016217 | -0.016106 | -0.016154 | -0.016201 | -0.016249 | -0.016296 | -0.016344 | -0.016391 | -0.016471 | -0.016621 | -0.016771 | -0.016921 | -0.017072 | -0.017075 | -0.017007 | -0.016939 | -0.01687 | -0.016802 | -0.016734 | -0.016773 | -0.016875 | -0.016973 | -0.017053 | -0.017098 | -0.017132 | -0.017167 | -0.017201 | -0.017201 | -0.017193 | -0.017185 | -0.017122 | -0.017027 | -0.016927 | -0.016723 | -0.01652 | -0.0077932 | 0 | 0
 | 0 | 0 | 0.0074285 | 0.018077 | 0.018542 | 0.018726 | 0.018834 | 0.018933 | 0.019011 | 0.019042 | 0.019074 | 0.019099 | 0.019084 | 0.019069 | 0.019054 | 0.019032 | 0.018984 | 0.01891 | 0.01882 | 0.01873 | 0.018639 | 0.018549 | 0.01848 | 0.018425 | 0.018369 | 0.018314 | 0.018258 | 0.018176 | 0.018076 | 0.017981 | 0.01794 | 0.017898 | 0.017857 | 0.017815 | 0.017774 | 0.017732 | 0.017691 | 0.01769 | 0.017708 | 0.017728 | 0.017747 | 0.017765 | 0.017783 | 0.01781 | 0.017781 | 0.017845 | 0.017908 | 0.017954 | 0.017988 | 0.018021 | 0.018054 | 0.018079 | 0.018049 | 0.018019 | 0.017989 | 0.01236 | 0.0058443 | 0 | 0
Velocity profile at 40 sec. | 0 | 0 | 0.00077853 | 0.0016529 | 0.0024687 | 0.0026131 | 0.0027576 | 0.0029021 | 0.0030908 | 0.0032946 | 0.0034986 | 0.0037028 | 0.0039425 | 0.0041826 | 0.0044221 | 0.0046912 | 0.004946 | 0.0052168 | 0.005488 | 0.0057596 | 0.0060317 | 0.0063043 | 0.0066075 | 0.0068931 | 0.0071786 | 0.0074642 | 0.0077497 | 0.0080353 | 0.0083208 | 0.0085899 | 0.0088224 | 0.0090548 | 0.0092873 | 0.0095197 | 0.0097504 | 0.0099801 | 0.01021 | 0.01044 | 0.010669 | 0.010899 | 0.011103 | 0.011292 | 0.011479 | 0.011658 | 0.011794 | 0.011918 | 0.012041 | 0.012164 | 0.012245 | 0.012317 | 0.012389 | 0.01243 | 0.012452 | 0.012473 | 0.012443 | 0.012414 | 0.0058614 | 0 | 0
 | 0 | 0 | 0.0046091 | 0.011216 | 0.011284 | 0.011171 | 0.010936 | 0.010681 | 0.010386 | 0.0099941 | 0.0096021 | 0.0091934 | 0.0086741 | 0.0081542 | 0.0076341 | 0.007091 | 0.0064626 | 0.0058398 | 0.0052204 | 0.0046009 | 0.0039815 | 0.0033621 | 0.0027261 | 0.0020796 | 0.0014331 | 0.0007866 | 0.0001401 | -0.00060531 | -0.0014118 | -0.0022157 | -0.0029805 | -0.0037453 | -0.0045101 | -0.0052749 | -0.0060397 | -0.0068045 | -0.0075693 | -0.008324 | -0.0091974 | -0.010094 | -0.010988 | -0.011881 | -0.012773 | -0.013599 | -0.014361 | -0.015118 | -0.015875 | -0.016628 | -0.017176 | -0.017719 | -0.018261 | -0.018764 | -0.01902 | -0.019275 | -0.019531 | -0.013445 | -0.0063567 | 0 | 0
Velocity profile at 60 sec. | 0 | 0 | -0.0035806 | -0.0076037 | -0.011296 | -0.011181 | -0.011065 | -0.01095 | -0.010708 | -0.010422 | -0.010136 | -0.0098494 | -0.0094223 | -0.0089673 | -0.0085124 | -0.0080573 | -0.0075759 | -0.0070121 | -0.006447 | -0.0058805 | -0.0053127 | -0.0047435 | -0.0042589 | -0.0038034 | -0.0033479 | -0.0028924 | -0.0024369 | -0.0019814 | -0.0015258 | -0.001079 | -0.00065133 | -0.00022369 | 0.00020395 | 0.00063159 | 0.0010512 | 0.0014668 | 0.0018824 | 0.002298 | 0.0027135 | 0.0031291 | 0.0035435 | 0.0039571 | 0.0043712 | 0.0047875 | 0.0051475 | 0.0054905 | 0.0058333 | 0.006176 | 0.0064299 | 0.0066646 | 0.0068991 | 0.007071 | 0.0072065 | 0.0073386 | 0.0073918 | 0.007445 | 0.0035179 | 0 | 0
 | 0 | 0 | 0.0042756 | 0.010405 | 0.010528 | 0.010485 | 0.010374 | 0.010253 | 0.010106 | 0.0099012 | 0.0096958 | 0.0094795 | 0.0091901 | 0.0089005 | 0.0086107 | 0.0083079 | 0.0079568 | 0.0076112 | 0.007269 | 0.0069268 | 0.0065846 | 0.0062425 | 0.0058877 | 0.005525 | 0.0051622 | 0.0047994 | 0.0044367 | 0.004042 | 0.0036276 | 0.0032156 | 0.0028381 | 0.0024607 | 0.0020832 | 0.0017058 | 0.0013284 | 0.00095093 | 0.00057349 | 0.00017673 | -0.00026472 | -0.00071275 | -0.0011594 | -0.0016047 | -0.0020485 | -0.002442 | -0.0027838 | -0.0031273 | -0.003471 | -0.0038135 | -0.0040254 | -0.0042339 | -0.0044421 | -0.0046336 | -0.0047207 | -0.0048078 | -0.0048949 | -0.0033718 | -0.0015941 | 0 | 0

## Slide 15: V velocity animation (Hover over and click play)

## Slide 16: Geometry modified: An annular tube section is placed in the shell

## Slide 17: Geometry modified: Flow path

## Slide 18: Velocity profiles in the inner shell section
Chart: Velocity profile in the inner shell at 1.25 In. from the bottom of the geometry. Flow through inlet: 1 Gpm
| -0.74200892399999996 | -0.72813952000000004 | -0.71427017500000001 | -0.70040077000000001 | -0.68653142499999997 | -0.67266201999999997 | -0.65879267500000005 | -0.64492327000000005 | -0.63105392500000002 | -0.61718452000000001 | -0.60331517499999998 | -0.58944588899999995 | -0.57557654400000002 | -0.56170719899999999 | -0.54783785299999999 | -0.53396850799999995 | -0.52009916300000003 | -0.506229818 | -0.49236050199999998 | -0.47849118699999998 | -0.46462184200000001 | -0.45075249699999997 | -0.436883152 | -0.42301383599999998 | -0.409144491 | -0.39527514600000002 | -0.38140583
20 sec | 0 | -0.2288 | -0.23635 | -0.24389 | -0.24901 | -0.25401 | -0.25832 | -0.26135 | -0.26438 | -0.26675 | -0.26756 | -0.26831 | -0.26878 | -0.26938 | -0.26965 | -0.26827 | -0.26714 | -0.26599 | -0.2644 | -0.26093 | -0.25741 | -0.2521 | -0.24619 | -0.2386 | -0.22948 | -0.1543 | 0
 | 0 | 0.039243 | 0.057334 | 0.056272 | 0.055027 | 0.053576 | 0.052136 | 0.050736 | 0.049334 | 0.04804 | 0.046736 | 0.045433 | 0.044212 | 0.043188 | 0.042696 | 0.042204 | 0.041608 | 0.040743 | 0.040124 | 0.039589 | 0.039056 | 0.038485 | 0.037902 | 0.037322 | 0.036691 | 0.036066 | 0
30 sec | 0 | -0.1975 | -0.196 | -0.19449 | -0.18932 | -0.18396 | -0.1777 | -0.16976 | -0.16181 | -0.15385 | -0.14594 | -0.13805 | -0.13022 | -0.12236 | -0.1144 | -0.10584 | -0.097269 | -0.088841 | -0.080235 | -0.069762 | -0.059253 | -0.049196 | -0.039285 | -0.030017 | -0.021345 | -0.011896 | -0.0017828
 | 0 | -0.040698 | -0.061523 | -0.06503 | -0.068491 | -0.071899 | -0.075237 | -0.078348 | -0.081459 | -0.084031 | -0.086399 | -0.088767 | -0.09107 | -0.093183 | -0.09473 | -0.096278 | -0.097838 | -0.099451 | -0.10041 | -0.10111 | -0.1018 | -0.10191 | -0.10169 | -0.10141 | -0.099734 | -0.098059 | 0
40 sec | 0 | -0.26093 | -0.26517 | -0.26941 | -0.26984 | -0.27007 | -0.26942 | -0.26711 | -0.2648 | -0.26203 | -0.2582 | -0.25442 | -0.25073 | -0.24677 | -0.24276 | -0.23809 | -0.23309 | -0.22811 | -0.22274 | -0.21546 | -0.20819 | -0.20013 | -0.19182 | -0.18287 | -0.17334 | -0.11574 | 0
 | 0.0047725 | 0.033686 | 0.049409 | 0.048949 | 0.048189 | 0.047092 | 0.04592 | 0.044508 | 0.043095 | 0.041813 | 0.040587 | 0.039361 | 0.037787 | 0.036188 | 0.03549 | 0.034792 | 0.033719 | 0.032544 | 0.031555 | 0.030663 | 0.02977 | 0.028882 | 0.028002 | 0.02713 | 0.026373 | 0.025619 | 0
50 sec | 0 | -0.19478 | -0.19689 | -0.199 | -0.19858 | -0.19803 | -0.19687 | -0.19459 | -0.19231 | -0.18972 | -0.18647 | -0.18324 | -0.17967 | -0.17538 | -0.17123 | -0.16777 | -0.16419 | -0.16072 | -0.15703 | -0.15159 | -0.14617 | -0.14033 | -0.13434 | -0.12803 | -0.12144 | -0.081095 | 0
 | -0.0002467 | -0.0017786 | -0.0030195 | -0.0038449 | -0.0045798 | -0.005214 | -0.0057442 | -0.0059595 | -0.0061714 | -0.0056674 | -0.0048698 | -0.0040722 | -0.0035548 | -0.0030146 | -0.0015793 | -0.00014401 | 0.0014013 | 0.0027889 | 0.0046884 | 0.0068371 | 0.0089807 | 0.01122 | 0.013504 | 0.015762 | 0.017739 | 0.019706 | 0
60 sec | 0 | -0.26875 | -0.27322 | -0.27769 | -0.2781 | -0.2783 | -0.2776 | -0.27522 | -0.27283 | -0.27015 | -0.26677 | -0.2634 | -0.25991 | -0.25629 | -0.25242 | -0.24711 | -0.24185 | -0.2366 | -0.23085 | -0.22274 | -0.21461 | -0.20554 | -0.19615 | -0.18609 | -0.17542 | -0.11679 | 0
 | 0.0005945 | 0.0041951 | 0.0055432 | 0.0041295 | 0.0025348 | 0.00073553 | -0.0010294 | -0.0026829 | -0.0043407 | -0.0054241 | -0.0064459 | -0.0074678 | -0.0082414 | -0.0087187 | -0.0087485 | -0.0087783 | -0.0087089 | -0.0080632 | -0.0070361 | -0.0058311 | -0.0046214 | -0.0031521 | -0.0015332 | 9.924e-05 | 0.0018062 | 0.0035192 | 0.0019076

## Slide 19: Geometry modified: An annular tube section is placed in the shell and two inlets are added
A geometry was made with two 0.25 In. ID inlets
The inlets are symmetric about the axis of the feedthrough

## Slide 20: Velocity profiles in the inner shell section
Chart: Velocity profile in the inner shell at 1.25 In. from the bottom of the geometry. Flow through each inlet: 1 Gpm
| -0.74200892399999996 | -0.72813952000000004 | -0.71427017500000001 | -0.70040077000000001 | -0.68653142499999997 | -0.67266201999999997 | -0.65879267500000005 | -0.64492327000000005 | -0.63105392500000002 | -0.61718452000000001 | -0.60331517499999998 | -0.58944588899999995 | -0.57557654400000002 | -0.56170719899999999 | -0.54783785299999999 | -0.53396850799999995 | -0.52009916300000003 | -0.506229818 | -0.49236050199999998 | -0.47849118699999998 | -0.46462184200000001 | -0.45075249699999997 | -0.436883152 | -0.42301383599999998 | -0.409144491 | -0.39527514600000002 | -0.38140583
20 Sec | 0 | -0.14358 | -0.14704 | -0.1505 | -0.15255 | -0.15452 | -0.15609 | -0.15691 | -0.15773 | -0.1583 | -0.15831 | -0.15832 | -0.15831 | -0.15821 | -0.15805 | -0.15758 | -0.15713 | -0.15667 | -0.15597 | -0.15427 | -0.15256 | -0.15035 | -0.14798 | -0.14509 | -0.14175 | -0.096032 | 0
 | 0 | -0.12196 | -0.1816 | -0.1859 | -0.18943 | -0.19209 | -0.19443 | -0.19572 | -0.19702 | -0.19739 | -0.19748 | -0.19758 | -0.19768 | -0.19758 | -0.19662 | -0.19567 | -0.19482 | -0.19403 | -0.19259 | -0.19084 | -0.1891 | -0.18663 | -0.18376 | -0.18084 | -0.17662 | -0.1724 | 0
30 sec | 0 | -0.24321 | -0.24761 | -0.25202 | -0.25377 | -0.25538 | -0.2564 | -0.25631 | -0.25621 | -0.25571 | -0.25428 | -0.25288 | -0.25145 | -0.24981 | -0.24809 | -0.24577 | -0.24331 | -0.24084 | -0.23806 | -0.23395 | -0.22986 | -0.22502 | -0.21994 | -0.21416 | -0.20775 | -0.14028 | 0
 | 0 | -0.11952 | -0.17781 | -0.18169 | -0.185 | -0.18769 | -0.19018 | -0.19205 | -0.19391 | -0.19491 | -0.19564 | -0.19637 | -0.19719 | -0.1979 | -0.19794 | -0.19798 | -0.19793 | -0.19785 | -0.19719 | -0.19628 | -0.19536 | -0.19361 | -0.19139 | -0.18908 | -0.1851 | -0.18111 | 0
40 Sec | 0 | -0.24377 | -0.25071 | -0.25764 | -0.26149 | -0.26516 | -0.26803 | -0.26938 | -0.27074 | -0.27167 | -0.27159 | -0.27149 | -0.27113 | -0.27046 | -0.26971 | -0.26852 | -0.26744 | -0.26636 | -0.26497 | -0.26224 | -0.25949 | -0.25574 | -0.25166 | -0.24645 | -0.24024 | -0.16259 | 0
 | 0 | -0.13611 | -0.20261 | -0.2073 | -0.21111 | -0.21395 | -0.21644 | -0.21782 | -0.2192 | -0.21977 | -0.21998 | -0.22019 | -0.22035 | -0.22028 | -0.21952 | -0.21875 | -0.21789 | -0.21725 | -0.21547 | -0.21321 | -0.21095 | -0.20785 | -0.2043 | -0.20066 | -0.19538 | -0.19009 | 0
50 Sec | 0 | -0.076511 | -0.12365 | -0.17085 | -0.17259 | -0.17432 | -0.17606 | -0.1778 | -0.17896 | -0.17981 | -0.18067 | -0.18152 | -0.18238 | -0.18296 | -0.18317 | -0.18339 | -0.1836 | -0.18381 | -0.18403 | -0.18412 | -0.18397 | -0.18381 | -0.18366 | -0.18351 | -0.18334 | -0.1831 | -0.18282 | -0.18253 | -0.18224 | -0.18196 | -0.18145 | -0.18105 | -0.18072 | -0.18038 | -0.18004 | -0.1797 | -0.17937 | -0.17901 | -0.17824 | -0.17746 | -0.17667 | -0.17589 | -0.17504 | -0.17392 | -0.1728 | -0.17168 | -0.17055 | -0.16903 | -0.16735 | -0.16566 | -0.16397 | -0.12893 | -0.081448 | 0
 | 0 | -0.092552 | -0.14723 | -0.18902 | -0.19247 | -0.19591 | -0.19936 | -0.20264 | -0.20549 | -0.20834 | -0.21119 | -0.21403 | -0.21649 | -0.21884 | -0.2212 | -0.22356 | -0.22592 | -0.22747 | -0.2289 | -0.23032 | -0.23174 | -0.23317 | -0.23459 | -0.23601 | -0.23742 | -0.23883 | -0.23987 | -0.24075 | -0.24163 | -0.24252 | -0.24339 | -0.24425 | -0.24504 | -0.24582 | -0.24659 | -0.24692 | -0.24702 | -0.24711 | -0.24721 | -0.24731 | -0.2474 | -0.24693 | -0.246 | -0.24507 | -0.24413 | -0.2432 | -0.24175 | -0.23932 | -0.23688 | -0.23445 | -0.23201 | -0.16831 | -0.10425 | 0
60 Sec | 0 | -0.14734 | -0.1512 | -0.15505 | -0.15741 | -0.1597 | -0.16154 | -0.16255 | -0.16357 | -0.16428 | -0.1643 | -0.16434 | -0.16437 | -0.16428 | -0.16414 | -0.16364 | -0.16312 | -0.16257 | -0.16176 | -0.1598 | -0.15785 | -0.15538 | -0.15274 | -0.14958 | -0.14597 | -0.098842 | 0
 | 0 | -0.1194 | -0.17779 | -0.18199 | -0.18549 | -0.18821 | -0.19062 | -0.19208 | -0.19354 | -0.19405 | -0.19425 | -0.19446 | -0.19468 | -0.19472 | -0.19397 | -0.19323 | -0.1926 | -0.19202 | -0.19082 | -0.18935 | -0.18788 | -0.18571 | -0.18318 | -0.18058 | -0.17668 | -0.17278 | 0

## Slide 21: Pressure drop through the geometry
For a total flow of 2 Gpm through the geometry (1 Gpm per inlet), the pressure drop is 12.98 Psid.

## Slide 22: Animation (Hover over and click play)
1 Gpm through each inlet
1 Gpm through one top inlet

## Slide 23: Results
Enhanced flow along the feedthrough in the model with vertical inlet.
Reversing flow predicted along the feedthrough in the model where the inlet and outlet were in the same plane.
With no gap between the feedthrough and the shell, the Y velocities observed in the region of interest are very low. On the order of 0.04 m/s.
Annular geometry with two inlets at the top results in highest velocity (~0.25 m/s (0.82 ft/s) and more symmetric velocity profiles in the bottom portion of the geometry.
Future iterations:
  Increase the length of the annulus region
  Add one more inlet?

## Slide 24: Future work: Adding more detail to the geometry
Inlets
Outlet
Outlet

## Slide 25: Future work: Adding more detail to the geometry
Feedthrough
Annulus
Outer shell
Feedthrough
Need efficient circulation in this region

## Slide 26: Future work: Desired flow pattern
Inlet
Inlet
Outlet
Outlet