## Sheet1
ID | Heading | Current requirement | Rationale | Proposed requirement | Comments
FSCF-Engr-021 | Condensation | FSCF shall ensure a minimum of 15,000 cfm per detector module or one air change per hour per cavern for both detector caverns (four chambers) and the CUC | Analysis work indicates that this will prevent condensation formation along the bottoms and sides of the cryostats | FSCF shall provide a minimum exhaust rate of 15,000 cfm per detector chamber along with an exhaust duct to the 4910 L for condensation purposes | With the rock septum removed, are we still requiring two drops to 4910 in each cavern of 15000 cfm? I think this is the case. -JF
New | Air supply for ODH | N/A | N/A | FSCF shall provide provide a minimum of 15,000 cfm per each detector cavern (a cavern is two detector chambers) for ODH purposes | See above, I believe this will be 2 x 15000 cfm? - JF
FSCF-Engr-041 | Far Detector Installation | FSCF shall ensure that a portion of the area above the rock septum, a volume defined as 14.4m W x 5m H x 10m L, with the 15m side aligned with the cavern transverse centerline, shall remain clear of utilities to allow installation of a temporary clean room. | Cannot have any utilities passing through this space to allow installation of the clean room. | FSCF shall excavate and remove the rock septum | Maybe add a note that any services planned for this space should be routed under or along the bridge planned at 4850 that will span the N /S to the CUC drift. -JF
FSCF-Engr-033 | Detector Cavern Dimensions | FSCF shall ensure that the detector Cavern width, height and length are in agreement with drawing F10043159 | Cryostat size plus minimum 1 foot clear space annulus defines minimum cavern size | FSCF shall excavate the detector chambers to dimensions shown in interface drawing F10043159
New | Electric power distribution in the mezzanine area | N/A | N/A | FSCF shall provide 62 kW of electric power distribution in the mezzanine area for use by the cryogenics sub-project per docdb-6566 | Do we need to be more specific on where? - JF
New | Electric power distribution in the LAr pump space | N/A | N/A | FSCF shall provide 56.25 kW of electric power distribution in the LAr pump space for use by the cryogenics sub-project per docdb-6566 | Is this for both cryostats or only one? If it is for two we should be specific on the locations for the placement of the power. - JF This is for one cryostat (i.e. 4 pumps per cryostat) - ND
New | Electric power distribution in the Central Utility Cavern (CUC) | N/A | N/A | FSCF shall provide 62 kW of electric power distribution in the CUC for use by the cryogenics sub-project as per docdb-6566 | We need to put the location of this on the envelope drawing to be clear of the location. For the these three power related requirements, a drawing would be very helpful. - JF
FSCF-Engr-148 | Compressed air supply for mezzanine, LAr pump space and the Central Utility Cavern (CUC) | FSCF shall provide supply of dry compressed air in the caverns at a pressure of 120 psig | This utility will be needed to operate the pneumatic valves, air powered tools, clean pieces after machining before installation, etc. | FSCF shall provide compressed air supply for the mezzanine, LAr pump space and the Central Utility Cavern (CUC) for use by cryogenics sub-project, at a pressure of 120 psig. The minimum requirement is 220 CFM at 90 psig | See above notes above on placement. - JF
New | Compressed air supply for surface compressor building | N/A | N/A | FSCF shall provide compressed air supply for the surface compressor building for instrumentation | Quantify and locate. - JF
FSCF-Engr-011 | Central Rock Platform, air-tight isolation | FSCF shall provide air-tight isolation below the rock septum floor elevation between the two detector module chambers in a cavern, both during excavation phasing and after construction. | This protects cryostat construction during excavation and ensures that an issue with one detector does not affect another during operation. | N/A | I assume this is the cryogen gas barrier we have been discussion. This will be added during one of the phases of occupancy of the 4910 level. This could be removed from FSCF and added elsewhere. - JF
New | Concrete slab moisture requirement | N/A | Denying the slab access to water is critical to the performance of the detector grounding system, and therefore the detector | The concrete of the slab under each cryostat warm structure shall be kept dry | T Shaw and T Lundin
FSCF-Engr-007 | Cavern Moisture | FSCF shall provide drainage and sumps sufficient to prevent standing water accumulation on cavern slabs on grade. Visible moisture appearing after the application of shotcrete does not require mitigation. | The interior of cavern shotcrete walls and concrete slabs on grade shall provide systems to manage water penetration to inner surfaces. Some moisture is acceptable and will be managed locally by the experiment as necessary.
New | Underground Data Processing room cooling water |  |  | Cooling Water shall be provided by CF to the Underground Data Processing Room. Chilled water provided should be sufficient to handle the anticipated 500 KW of power dissipated in the room. | T Shaw
New | Underground Data Processing room fire suppression |  |  | The Underground Data Processing Room shall use a dry chemical fire suppression system. (I could not find a requirement which specifically stated this.) | T Shaw. My comment is to say that fire suppression for electronics is necessary and let the A/E decide what the media is. - JF FSCF-Engr-058 states the fire suppression for Detector chambers shall be pre-action type - ND
FSCF-Engr-093 |  | FSCF shall provide a surface data transfer room with space, power (30 kVA), and cooling for a minimum of 6 data racks |  | the DAQ Consortia would like this changed to 50KVA power and 8 data racks | T Shaw Is 8 enough? - JF
FSCF-Engr-124 |  | “FSCF shall provide space for an estimated 52 racks for the DAQ systems, along with power and cooling for the racks” and Docdb 208 requests 500KVA for what is now referred to as the Underground Data Processing Room. |  | DAQ Consortia would like to reserve the entire 500KVA budget for the Racks. No utilities (lights, cooling, etc.) should cut into this budget. | T Shaw
FSCF-Engr-161 |  | FSCF shall provide chilled water to a distribution supply and return manifold along the length of each detector chamber with control valves every ~2.3m for a total of 25 connection points, each designed to support 3 electronics racks” |  | We need to add the requirement that this is deionized water and can handle 500KW per detector. Jim Stewart suggests a better spacing for connections would be the beam spacing of 1.6m. | T Shaw
FSCF-Engr-154 | Cryostat loading | FSCF shall provide a concrete floor for seating the cryostat that will withstand the cryostat loading |  | In progress, new installation scheme being discussed | Will be covered in April workshop - JF
New | Bridge across cavern (North-South) | N/A | N/A | FSCF shall construct a bridge across the cavern in the North-South direction | Loading and clear height from 4910 level is still needed. -JF Does this include to runway rails for a bridge crane included under the bridge? 2 tons? Removable railings?
New | Utilities along North-South drift | N/A | N/A | FSCF shall route the utilities underneath the North-South bridge | See note above on FSCF-Engr-041 - JF
FSCF-Engr-003 | Anchorages on rock septum for bridge support | FSCF shall provide anchorages into rock for cryostat supplied bridges to be placed between each cryostat and the septum to allow future access to top of cryostat | Anchorage to the rock pillar and/or the side walls to support a bridge of whatever size necessary for the detector assembly. | N/A | Does this need to be added to the bridge requirement? - JF Side paths are required between the bridge and cryostat. The main bridge should be designed to accommodate these. Quantity location and loading?