## Slide 1
S. Dixon\R. Wielgos
Conventional Facilities
29-August-2018
Preliminary Design Review
WBS 121.06.02 – Site Preparation

## Slide 2: Agenda
Charge
Review Requirements
Overview (by Gensler Team)
Summary
Next Steps

## Slide 3: Charge
Please review the information for appropriateness of the proposed systems, impacts on existing systems and operations, specific technical requirements to be incorporated into the design and compliance with best and required practices of authority having jurisdiction.

## Slide 4: Review Requirements
  From PIP-II Project Design Review Plan

## Slide 5: Organizational Structure

## Slide 6: Design Team

## Slide 7: Scope
The Site Preparation scope includes the following phases:
Phase 1 – Site Clearing
This is the work that is required to generally prepare the site for future work packages
Installation of erosion controls (silt fence);
Tree removal;
Installation of temporary road;
Topsoil striping and stockpile;
Sedimentation pond;
Pond crossing;
Phase 2 – Utility Corridor (completed prior to Cryo Plant Building completion)
This extends the existing utilities to the project site including:
Electrical ductbanks, manholes, feeders and 4-way air switches;
Communication ductbank and manholes;
Industrial cooling water;
Domestic water supply
Sanitary sewer system;
Chilled water;
Storm sewer;
Make up water connection;

## Slide 8: Scope
The Site Preparation scope includes the following phases:
Phase 3 – Site Work (Completed after Cryo Plant Building but before Linac Complex)
This work includes:
Final grading outside of building zone;
Roadway subgrade;
AZero pond modifications;
Entry roads at ponds;
Utilities west of Linac Complex
Modifications to Main Ring Road and South Booster Road
Phase 4 – Site Restoration
This work includes:
Site restoration and landscaping;
Final asphalt and grading;
Site Lighting.

## Slide 9: Deliverables
This submittal must convey a level of completeness that demonstrates the project is on schedule and on budget. This submittal will contain, as a minimum, the following:
Drawings that convey the proposed design and major systems, but need not have all of the notes and details of the final product;
Outline specification;
The deliverables will include an estimate of construction cost and a schedule for the construction with pacing milestones and dates;
A list of materials, if needed, that require exemption to the Buy American Act;
Submittal shall be in PDF format plus the associated AutoCAD DWG files, REVIT models, Word and Excel files;
The submittal will include documentation of compliance with DOE’s Guiding Principles.

## Slide 10: Technical Requirements
Technical Requirements Specifications ED0006789

## Slide 11: Changes to KPP
Threshold and Objective KPP – No Changes
  KPP from PIP-II Preliminary Project Execution Plan (PIP-II-doc-115)

## Slide 12: Changes to FRS - No Changes
  Functional Requirements Specification can be found at TeamCenter ED0006787

## Slide 13: Safety by Design

## Slide 14: Code Compliance
Organizational Processes provide institutional requirements for the design, construction and operations of all projects built and operated at Fermilab. All applicable DOE orders and standards are included in these requirements.
DOE Order 151.1C – Comprehensive Emergency Management System;
DOE Order 413.3B – Program and Project Management for the Acquisition of Capital Assets, Change 1 issued 11/29/10;
DOE Order 414.1C – Quality Assurance;
DOE Order 420.1B – Facility Safety;
DOE Order 430.1B – Real Property Asset Management (2/8/08);
DOE Order 430.2B – Departmental Energy, Renewable Energy and Transportation Management;
DOE Order 450.1A – Environmental Protection Program (6/4/08);
DOE STD-1066-99 – Fire Protection Design Criteria;
DOE STD-1073-2003 – Configuration Management;
DOE Guide 420.1-2 – Guide for the Mitigation of Natural Phenomena Hazards for DOE Nuclear Facilities and Non-Nuclear Facilities;
10 CFR 835 – Radiological Protection Program;
10 CFR 851 – Worker Safety and Health Program;
10 CRF 851.23 – Safety and Health Standards;
Internal Fermilab permits and work notifications as described in the Fermilab ES&H Manual (FESHM)
Fermilab Director’s Policy Manual (http://www.fnal.gov/directorate/Policy_Manual.html);
Fermilab Engineering Manual (http://www.fnal.gov/directorate/documents/FNAL_Engineering_Manual.pdf)

## Slide 15: Code Compliance
International Building Code (IBC) – 2015 Edition
International Energy Conservation Code – 2009 Edition
International Fire Code – 2009 Edition
International Mechanical Code – 2009 Edition
Minimum Design Loads for Buildings and Other Structures – ASCE 7-05
Building Code Requirements for Structural Concrete – ACI 318-05
Specification for Structural Steel Buildings – AISC 360-05
Building Code Requirements for Structural Concrete and Commentary – ACI 318-08
Illinois Plumbing Code – 2004
Illinois Department of Public Health Codes
Illinois IEPA
NFPA 101 Life Safety Code – 2009 Edition
NFPA 24 – Standard for the Installation of Private Fire Service Mains and Their Appurtenances – 2010 Edition
NFPA 70 – National Electrical Code – 2008 Edition
NFPA 70E – Standard for Electrical Safety in the Workplace – 2009 Edition
NFPA 110 – Emergency and Standby Power Systems – 2010 Edition
ANSI/ASME B31.3 – Process Piping (2002)
ANSI 31.9 – Building Services Piping (1996)
Occupational Safety and Health Administration (OSHA)
Underwriters Laboratory
ICC/ANSI A117.1 – 2003 Standard for Accessible and Usable Buildings and Facilities Illinois Accessibility Code
ADA Accessibility Guidelines for Buildings and Facilities (ADAAG) – 2004 will be used for those areas of facility not exempted by Fermilab policy
Illinois Accessibility Code
Enterprise standards from regulatory agencies, code bodies and trade organizations also provide requirements for the design and construction of the PIP-II conventional facilities.

## Slide 16: Risk Assessment
  From ED0008276

## Slide 17: Risk Register

## Slide 18: Engineering Design and Analysis
Stakeholder Requirements
A/E Design Team
  Gensler - Architecture
  CMT - Site Civil
  TGRWW - Structural
  IMEG - Electrical, Mechanical
  Hoerr Schaudt - Landscape Architecture
  Turner - Constructability, Cost Estimates

## Slide 19: Preliminary Software Requirements
Not applicable

## Slide 20: Reliability and Maintainability Requirements
Included in the Engineering Design and Analysis
  Site Layout, Landscaping, Roadways, Drainage
    Slopes
    Drainage
    Traffic
  Utility Corridor
    ICW, LCW, Chilled Water
      Looped Systems
      Isolation Valves
      Material Selection
    Electric Power, Communications
      Ductbank & Manhole Systems
      Switches
      Looped Feeds

## Slide 21: Plan for Obtaining Safety Approvals
Radiation Safety
      Engage Radiation Safety with the Required Documentation Through FESS for Beamline Construction Approvals
Review Comments
Notice to Proceed Authorization
      Quality Control Plan
      Soil Erosion and Sediment Control Plan
      Project Hazard Analysis

## Slide 22: Preliminary QA/QC Plan
PIP-II Preliminary QA Program
(PIP-II-doc-142)
Design Phase
Q/A requirements are included in A/E tasking;
The Gensler team provides QA/QC following the internal corporate process;
Design Review by Fermilab Subject Matter Experts

## Slide 23: Lessons Learned – Other Projects
UUP - Site Specific Construction Safety Plan
      Flow down all necessary requirements of the construction project to the subcontractors during the bid phase.
UUP - Design Phase Utility Locates
      It was advantageous to gather as much information of the potential utility conflicts between existing utilities (where known) and proposed piping during the design phase versus during construction.
UUP - Master Substation Excavation Limit ORPS
      Work was halted immediately after a small area was dug, and an investigation took place on the cause for the overexcavation. The limits of the excavation permit were not clearly marked in the field. Additional effort will be made to mark critical areas near beamlines.
UUP - Capturing GIS Data on Utilities During Excavation
      This data was then used to update existing data in the GIS Maps and will help build a robust database of information that can be used by future projects.

## Slide 24: Previous Review Action Items
None

## Slide 25: Preliminary Safety Hazard Assessment
Not applicable

## Slide 26: Baseline Cost and Schedule
Under development, available 04SEP18

## Slide 27: END

## Slide 28: Backup

## Slide 29: 121.06 - Scope Overview – Above Grade
Cryo Plant Building
Cold Box Station
Warm Compressor Station
Control Room
Exterior Space
Utility Plant Building
LCW Equipment
Control Room
Exterior Space
High Bay Building
Control Room
Computer Room/Conference Room
Tech Support Space
Upper High Bay
Lower High Bay
Mechanical/Electrical Space
Exterior Space
Linac Gallery
General Space
Half Wave Resonator
SSR1
SSR2
LB650
HB650
Beam Transfer Line PS
Exterior Space
Space descriptions based on Room Data Sheets

## Slide 30: 121.06 - Scope Overview – Below Grade
Booster Connection
Beamline
Beam Transfer Line
Beamline
Beam Absorber Space
Linac Tunnel
Half Wave Resonator
SSR1
SSR2
LB650
HB650
Space descriptions based on Room Data Sheets