## Slide 1: Cryogenics Plans and Interface with FSCF BMS – DRAFT
Mark Adamowski
David Montanari
LBNF/DUNE FS Interface Meeting
1 November 2018

## Slide 2: Detector Cavern ODH Safety System Local Inputs – 1/2
Oxygen level at 19.5%:
  Local cavern horn/strobes.
    Minimizing in series control components (i.e. non-safety PLC, etc.).
  ODH alarm to SURF PLC?
  ODH alarm to Ventilation PLC?
Oxygen level at 18.0%:
  Cryo isolation valves will close.
  LBNF Facility horn/strobes:
    This means CUC horn/strobes go off.
    Drift between detector/CUC?
    Other drifts?
  ODH emergency alarm to SURF PLC?
  ODH emergency alarm to Ventilation PLC?

## Slide 3: Detector Cavern ODH Safety System General Inputs – 2/2
Low air temperature:
  Cryo isolation valves will close.
  Low air T alarm to SURF PLC?
Seismic activity (above some acceleration value):
  Cryo isolation valves will close.
  Seismic alarm to SURF PLC?
Local Emergency stop:
  Anything significant here??

## Slide 4: Detector Cavern ODH Safety System Input from other systems
From Ventilation system:
  Low Exhaust flow:
    Sensor installed after beneficial occupancy?
    Same response as ODH 19.5%.
  Ventilation trouble alarm?
    Cryo isolation valves will close.
  Fire alarm:
    Cryo isolation valves will close.
From SURF:
  SURF facility alarm?
  Site alarm?
From DUNE:
  Anything that should trigger an ODH alarm?

## Slide 5: CUC ODH Safety System Local Inputs
Oxygen 19.5%:
  Local cavern horn/strobes.
    Minimizing in series control components (i.e. non-safety PLC, etc).
  ODH alarm to SURF PLC?
  ODH alarm to Ventilation PLC?
Oxygen 18.0%:
  Cryo isolation valves will close.
  LBNF Facility horn/strobes?
    Smaller cryogen inventory compared to cryostat.
    Drifts?
  ODH emergency alarm to SURF PLC?
  ODH emergency alarm to Ventilation PLC?

## Slide 6: CUC ODH Safety System General Inputs
Seismic activity (above some acceleration value):
  Cryo isolation valves will close
  N2 refrig safe shutdown?
  Seismic alarm to SURF PLC?
Local Emergency stop:
  Anything significant here??

## Slide 7: CUC ODH Safety System Input from other systems
From Ventilation system:
  Low Exhaust flow:
    Sensor installed after beneficial occupancy?
    Same response as ODH 19.5%
  Ventilation trouble alarm?
    Cryo isolation valves will close
  Fire alarm
    Cryo isolation valves will close
From SURF:
  SURF facility alarm?
  Site alarm?
  Power outage:
    Nitrogen system shuts down and start flowing LN2 from temporary storage.
    Controls system goes into safe mode.
From DUNE:
  Anything that should trigger an ODH alarm?

## Slide 8: Ross cage ODH Safety System
Concept battery powered ODH monitor/alarm
  Oxygen 19.5% - Alerts cage operator
    Operator returns cage to surface
    Safety/cryo investigates.
      Possible actions to mitigate
        Stop GAr transfer for filling
        N2 refrig to safe shutdown

## Slide 9: ODH sensors in drifts
ODH sensors planned for drifts containing liquid or gas cryogen piping.
  These are ODH 0 spaces. (ODH 0 status must be reevaluated with drift air flow from CF design.)
  These sensors inform LBNF safety PLC, SURF PLC, Ventilation PLC?

## Slide 10: Detector cavern safety PLC
Safety PLC
ODH Sensors
Seismic Sensors
Temperature Sensors
Exhaust flow Sensors
Local Horn /strobe
Alarms to cryo PLC
Alarms to other PLC

## Slide 11: Other alarms
Pressure increase in cryostat:
  Automatic vent will act automatically to release overpressure. If pressure reaches PSV set point, PSVs will release overpressure.
  Triggers alarm to cryo ops team or cryo expert on call for investigation.
Low vacuum level in vacuum insulation (> 10 mBar):
  Triggers alarm to cryo ops team or cryo expert on call for investigation.
High level of Oxygen/Water in GAr purges from chimneys.
  Triggers alarm to cryo ops team or cryo expert on call for investigation.
Argon in GN2 purge within insulation.
  Triggers alarm for investigation.
Nitrogen System malfunctioning:
  Triggers alarm to cryo ops team or cryo expert on call for investigation.
  If ODH alarm, same response as ODH alarm.
  Will start usage of LN2 storage to maintain Argon inventory.
Need to continue to identify data that needs to be exchanged with DUNE and FSCF/BMS.

## Slide 12: Thanks

## Slide 13: Backup

## Slide 14: Preliminary Control System Architecture