## Slide 1: Fluid Systems Design and Quality Assurance Management in Accelerator Applications
Maurice Ball
ESS Collaboration Meeting
8 November 2018

## Slide 2: Charge
Design and Quality Assurance Management in Accelerator Applications
This topic will include discussions about water quality management such as copper oxide production and control requirements and impact on accelerator operations reliability. This topic will also cover aspects of LCW system design and its impact on project management, including construction, scheduling, and layout of such systems.

## Slide 3: Outline
Overview of LCW and RAW Systems
Challenges of piping system Design, Installation, Commissioning, Operations
Radioactive Water (RAW)
Copper Oxide Particulate

## Slide 5: Overview
Typically Category D or Normal Fluid Systems under the ASME B31.3 Piping System code
Over 50+ LCW and RAW Systems
  Differential pressures ranging from 10 PSID to 300 PSID.
  System flows ranging from 5 GPM to 8000 GPM.
  Temperatures range from 80 F to 100 F
  Conductivities range 1 MOhm-cm to 18 MOhm-cm
Over 100 compressed air systems
  Instrument and shop air applications
  Moisture down to -40F
  Pressures cycle between 80 PSIG and 130 PSIG
Other fluid systems (Fluorinert, compressed gases)

## Slide 6: Small Systems (Skids) – Proton Source/LINAC

## Slide 7: Medium to Large Systems – Muon Campus Delivery Ring

## Slide 8: Systems of a Very Large Scale – Main Injector

## Slide 9: Challenges

## Slide 10: Engineering Design Process – Fermilab Engineering Manual
Requirements and Specifications
Engineering Risk Assessment
Requirements and Specifications Review
System Design
Engineering Design Review
Procurement and Implementation
Testing and Validation
Release to Operations
Final Documentation

## Slide 11: Issues We Have Experienced – Design of LCW Systems
Accelerator component fluid system engineers must be included in the design process of the accelerator components.
Getting up to date component information and drawings
Correct heat loads at actual operating conditions
Determining Resistivity ranges
Types/kinds of controls desired (i.e. temperature, pressure, dissolved oxygen, resistivity
Obtaining actual operating parameters/expectations.
Result: Incorrect or improperly sized equipment, schedule/milestone delays

## Slide 12: Issues We Have Experienced – Installation of LCW Systems
Timing issues, scheduling
Coordinating the timing of installation of components (i.e. power, interlocks, controls, piping
Coordinating with safety, radiation, manpower, and contractor requirements.
Communication with the stakeholders: landlords, safety, project engineers, and integration groups
Walkthroughs, toolbox meetings
Microbiologically Induced Corrosion (MIC)
Hydrostatic pressure testing very time consuming, especially for big systems. Testing in sections leads to a more thorough and streamlined process.
Result: schedule/milestone delays

## Slide 13: Issues We Have Experienced – Commissioning of LCW Systems
Timing issues, difficulty with start-up, trouble-shooting, and corrections, system balancing
Coordinating the timing of installation of components (i.e. power, interlocks, controls, piping
Coordinating with safety, radiation, manpower, and contractor requirements.
Pressure to get the accelerator machine operational
Effective communication, particularly at startup
Allowing time for verifying valves, system balancing
Result; component damage and safety problems

## Slide 14: Issues We Have Experienced – Operation of LCW Systems
Poor communication of failing equipment
Addressing issues immediately
Communicating the gradual decline or concerns.
Mismatch between stakeholder/user expectation and how the system was designed.
Viewing fluid system like a public utility instead of a critical process.
Systems tapped in without consequences.
Negotiating priority. Allowing time for trip/alarm limits validated
Result: Interruptions to operations, decreased system reliability

## Slide 15: Radioactive Water (RAW) Systems

## Slide 16: Radioactive Water (RAW) Systems
Isolated water systems
Normal Fluid Systems under the ASME B31.3 Piping System code
Specifically designed to cool highly radioactive devices or accelerator equipment.
Heat exchange with regular LCW or chill water systems
Sometimes with an intermediate system in between
Protects from cross contamination from radioactive water.

## Slide 17: Overview
Introduction to NuMI RAW systems
    Target Hall RAW room
    Target Hall DI room
    Absorber Hall RAW room (Not discussed here)
Auxiliary fluid systems for RAW systems
    Target RAW exchange system
    TGT, H1, and H2 Argon purge systems
    H1 and H2 spray nozzle high pressure Argon system
    Absorber RAW exchange system (Not discussed here)
  Future system: H2 sampling system for H1 and TGT RAW system

## Slide 18: Overview
Target, Horn 1, Horn 2, and Decay Pipe US RAW systems
Decay Pipe DS and Absorber RAW systems

## Slide 19: Overview of RAW systems
Target, Horn 1, Horn 2, and Decay Pipe RAW cooling systems are closed loop systems.
They provide cooling water to the above components. The water is maintained at a resistivity of 6-8 MOhm-cm.
There are full-flow filtration and De-Ionization (DI) loops on all of the systems.
There is a flow, pressure, level, temperature, resistivity, and exhaust gas flow (not on Decay pipe RAW) instrumentation package on all the systems.
There are other auxiliary fluid systems that support the RAW system:
  The Argon purge systems to displace the produced H2 gas.
  The RAW exchange system to maintain a low concentration of tritium in the RAW systems during operations.

## Slide 20: Overview: Plan view of Target Hall
Target
Horn 1
Horn 2
RAW room-Target Hall penetration (~28’ long)
Target RAW System
Decay Pipe US RAW System
Horn 1 RAW System
Horn 1 RAW System
Target Hall
(Chase)
Beam
RAW Room

## Slide 21: Overview: RAW and DI Rooms
Decay Pipe US RAW System
Horn 1 RAW System
Target RAW System
Horn 2 RAW System
Penetration to Target Hall
RAW system DI bottle casks
2013 upgrade

## Slide 22: Overview: RAW room
Decay Pipe US RAW System
Horn 1 RAW System
Target RAW System
Horn 2 RAW System

## Slide 23: Overview: DI Room
DI bottle casks for RAW Systems (6” thick walls)
RAW room behind this wall
Exchange system (Fill, make-up, drain RAW systems)
2013 upgrade

## Slide 24: Target RAW Exchange system
Fill and make-up operation: Fills( entire system vol) and makes-up RAW systems with fresh DI water
Stores RAW water from systems in this tank

## Slide 25: Target RAW Exchange system
During operations, try to maintain tritium concentration to values <=1E06 pCi/ml. This is not a hard limit.
This is done by draining some water from the RAW systems and adding fresh DI water on a weekly basis.
1 Million pCi/ml
1 Million pCi/ml
Source: Abhishek Deshpande, Tony Busch, and Matt Quinn

## Slide 26: TGT, H1, and H2 Ar purge systems
RAW system expansion tanks have low pressure Argon gas flowing into them.
This is to displace the H2 produced during beam operations. Outlets of the tanks open Target Hall Chase.
Above measurements are made during downtime (Sept. 25 2018) conditions with newly installed gas mass flow meters.
598 SccmAr
502 SccmAr
120 SccmAr
Target RAW
Horn 1 RAW
Horn 2 RAW

## Slide 27: Horn 1 and Horn 2 Spray Nozzle Ar purge systems
Argon is also induced through the Horn 1 and Horn 2 inner conductor water spray nozzles.
This Argon shows up on the exhausts of the H1 and H2 expansion tanks:
502 SccmAr
120 SccmAr
530 SccmAr
(Spray Line)
80 SccmAr
(Spray Line)
~1109 SccmAr
~210 SccmAr
Horn 1
Horn 2

## Slide 28: New instrumentation
A gas analyzer to measure H2, O2, and water vapor concentrations inside the head space of the RAW system expansion tanks will be purchased.
The sampling line infrastructure has been installed and tested during Shutdown 2018.

## Slide 29: Operational experience
DI bottles used to be in the RAW room. They have been upgraded, put into casks, and moved to the DI room in 2013. Less radiation in the RAW room. Prolongs the life of the bottles.
DI bottles have pre and post filters. Increases life of the bottle.
DI bottles not used continuously, 3-way valve loop maintains system resistivity between 6-8 MOhm-Cm. This also increases the life of the bottle.
Filter cartridges are changed every 4 months of beam-time. This too prolongs the life of the DI bottle.
Conventional off-the shelf process instrumentation fails due to radiation in the RAW room. Rad-hard instrumentation or instrumentation with remote signal conditioning capabilities is selected. A radiation map of the RAW room is created by placing dose monitors in various locations. This map is used to install instrumentation that is not rad-hardned.
Copper oxide is an issue with systems with copper piping: Decay Pipe RAW system. There are 3 full-flow filtration loops with 5 micron absolute filter cartridges. They are replaced every 4 months of beam-time.
In the copper systems, water is replaced every 2 years.
Argon purge on all the system expansion tanks prevents carbonic-acid and nitric acid formation.

## Slide 30: Copper Oxide

## Slide 31: History of the Copper Oxide Problem in Muon Campus (formerly Pbar)
  Oxygen introduced into the LCW system during maintenance activities combined with copper in solution to form copper oxide
  Copper oxide accumulates in the system and plugs narrow flow paths in water cooled devices
  Water cooled devices overheats.
  Shutdown accelerator operations, requiring intrusive back flushing procedures

## Slide 32: Copper Oxide

## Slide 36: Copper Oxide - Resolution
  Monitor, trending of oxygen and particulate levels via DO and TDS sensors
  Remove the oxygen, Prevent new oxygen from entering
  Remove copper oxide particulate, via full flow filtration

## Slide 37: Copper Oxide – Action Plan/Implementation
  Full-Flow Filtration (PIC)
  Maintenance Program

## Slide 38: Copper Oxide – Action Plan/Implementation
  Dissolved Oxygen/TDS Sensors (PIC)
  High maintenance
  Constant calibration

## Slide 39: Copper Oxide – Action Plan/Implementation
  Oxygen Removal Skid – Liqui-Cel Technology
  Uses Nitrogen gas to pull a vacuum through a cel membrane

## Slide 40: Summary
Fluid Systems require careful consideration, care, and respect.
Not just plumbing - “Its not just water”
Fluid systems are critical process systems.
Serious consideration must be taken regarding
  Design
  Installation
  Commissioning
  Operation
Other issues That Require Engineering Input/Consideration
  Radioactive Water (RAW) Systems
  Copper Oxide Mitigation

## Slide 41: References/Acknowledgements
The Chemistry Of Copper In Water And Related Studies Planned At The Advanced Photon Source - R. Dortwegt , Advanced Photon Source, Argonne National Laboratory, Argonne, IL 60439 E.V. Maughan, College of Knowledge; Duisburg, Germany D-47198
Experience With Copper Oxide Production In Antiproton Source Components At Fermi National Accelerator Laboratory- Christine R. Ader (FNAL), Elvin R. Harms, Jr. (FNAL), James P. Morgan (FNAL), Fermi National Accelerator Laboratory
Abhishek Deshpande, Fluids Machine Engineer, Beamlines and Muon Campus, AD/Mechanical Support Department, Fermi National Accelerator Laboratory
David Hixson, Fluids Machine Engineer, Proton Source and Main Injector/Recycler Machine, AD/Mechanical Support Department, Fermi National Accelerator Laboratory
Karl Williams, Deputy Head, Project Engineering Group, AD/Mechanical Support Department, Fermi National Accelerator Laboratory
Jerzy Czajkowski, Fluids Machine Engineer, Fermilab Accelerator Science and Technology (FAST) Facility, AD/Mechanical Support Department, Fermi National Accelerator Laboratory

## Slide 42
Questions?