## Slide 1
Cory Crowley, George Lolov, & Lionel Pittman
TSD Topical Meeting
2/28/2019
1MW Horn Stripline + Air Diverter Wind-Tunnel Testing

## Slide 2: Outline
2/28/19
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
Cory
  1MW Stripline Motivation & Requirements
  Testing & Design Goals
  T-Block Air Diverter
George
  Testing Setups
  Upgraded Diverter Design
  Data Acquisition / Analysis
Cory + George
  Current Status

## Slide 3: 1MW Stripline Motivation & Requirements
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
Existing 700kW stripline & air diverter system is not a viable solution at 1MW.
Max stripline temperature desired to be less than 100C at any point.
Must maintain 100,000,000 pulse lifetime requirement. Temperature & resultant material creep makes pulse life determination impossible.
Analysis Credit: Zhijing Tang
Must mate to existing NOvA Horn conductor flange geometry.
Improve material selection where possible (6013 aluminum).
Improve air cooling to stripline structure.
New Stripline
2/28/19

## Slide 4: Testing & Design Goals
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
Understand existing air flow characteristics & heat transfer.
Identify improvements to existing structures & verify through iterative theoretical & experimental testing.
Verify conclusions and final production design with repeat wind tunnel & heat transfer test.
Analysis Credit: Lionel Pittman
2/28/19

## Slide 5: CFD Conclusions of Existing Diverter
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
Provides good flow for inner lower flags; moderate flow for inner upper flags.
Sharp edges and pinch points appear to impeded air velocity.
Initial thoughts were that they created eddy currents to improve flow.
Theoretical simulations show these can be improved (George to discuss further).
Sharp Edges
Middle Duct
Outlet Duct
Inlet Duct
Divider
Mounting Bracket
Low Airflow
Low Airflow
2/28/19

## Slide 6: T-Block Air Diverter
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
Solution needed to address stripline upper flags and vertical side spans.
Two realistic solutions:
  Pipe air down through stripline block.
  Dedicate T-block with internal duct.
Internal duct chosen because of direct access to hot upper flags.
Air deflection from T-block appears to greatly help vertical side spans as well.
Multiple diverter angles tested; winner is 45 degrees at ~600 CFM.
2/28/19

## Slide 7: T-Block Air Diverter
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
Drop in replacement T-block.
Channel dimensions minimized (8” wide X 4” deep).
Labyrinth dogleg direction is opposite that of stripline block to minimize effect on shielding.
Supply fed through structural box beam support on beam left & will employ quick disconnect coupling.
2/28/19

## Slide 8: Test Setup - Pressure Testing Trials
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
Fixed on each of the 8 flag faces and measured airflow pressure at 9 locations on the flag surfaces
2/28/19

## Slide 9: Pressure Testing
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
Ran pressure tests for each iteration of the top and bottom diverters.
Results mostly inconclusive. Pressure drop not large enough to provide reliable data.
2/28/19

## Slide 10: Convection Coefficient Testing
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
Al coupon with heating pad and thermocouple inside.
Set on each of the flag faces, set to 80W, turned on the airflow, observed cooling curve.
Identical to original method used, with slightly improved thermal isolation of coupon.
2/28/19

## Slide 11: Old / New Diverter Comparison
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
Sharp Edges
Middle Duct
Outlet Duct
Inlet Duct
Divider
Mounting Bracket
Low Airflow
Low Airflow
Smooth Edges
Middle Duct
Outlet Duct
Inlet Duct
Divider
Mounting Bracket
Balanced Airflow
2/28/19

## Slide 12: New Diverter Design
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
New Inlet features 4 sheets curved into elliptical geometry.
Initially tried creating from cardboard- didn’t turn out so well.
Split into 4 sections and 3D printed – worked really well (Thanks Keith!)
2/28/19

## Slide 13: New Diverter Design: Inlet
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
DEVELOPMENT OF BELL MOUTH FOR LOW SPEED AXIAL FLOW
COMPRESSOR TESTING FACILITY
Apurva Tiwari Et al.
2/28/19

## Slide 14: New Diverter Design: Outlet
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
Because we doubled the inlet area, we also doubled the outlet area – airflow covers more flag surface area.
Didn’t bother with cardboard, split up into 4 pieces and 3D printed.
2/28/19

## Slide 15: Diverter Prototype
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
3D Printed Inlet
3D Printed Outlet
Cardboard Middle Section with Cardboard Divider
Highly Engineered Support Structure
Strategically Placed Counterweight using Principles of Statics
2/28/19

## Slide 16: Convection Coefficient Testing
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
Heating Pad
Adjacent Coupon
T
T
J-Type Thermocouple
3/8”
3/8”
3/8”
3/8”
3/8”
4.25”
4.25”
Assumed stagnant air convection coefficient between the striplines unless proven otherwise.
Simulations showed inner stripline temps to be too high.
Experimentally determined convection coefficient for most problematic areas.
2/28/19

## Slide 17: Convection Coefficient Testing
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
6 Total Tests – changed top/bottom diverter designs, added insulation.
Not all flags showed cooling at 80W, Wattage had to be adjusted to equilibrium.
2/28/19

## Slide 18: Updated Results
TSD Topical Meeting / 1MW Horn Stripline + Air Diverter Wind-Tunnel Testing
Steady state temperatures @ 1MW appear to meet requirements of <100C.
Hot spots are result of remaining conservative cooling coefficients. Further testing could reduce further but design goals are met.
Final FEA planned for March finish.
Final report to be released thereafter.
2/28/19