## Pivot Table
WBS Name | HPRF
Building | (All)
Cooling Type | (All)
Systems and Components | Sum of Quantity | Sum of Total Heat Load (KW) | Sum of Heat Load to Air from Cables (KW) | Sum of Total KVA | Sum of Total Power (KW) | Average of Uncertainty Multiplier
Circulators
HB650 | 36 | 0 |  | 0 | 0 | 5%
HWR | 8 | 0 |  | 0 | 0 | 5%
LB650 | 33 | 0 |  | 0 | 0 | 5%
SSR1 | 16 | 0 |  | 0 | 0 | 5%
SSR2 | 35 | 0 |  | 0 | 0 | 5%
Power Amplifiers
HB650 | 36 | 5085 |  | 7003.5821 | 6023.0806 | 37.5%
HWR | 8 | 126 |  | 119.7194 | 107.7474 | 5%
LB650 | 33 | 3151.5 |  | 3676.3818 | 3161.6883 | 37.5%
SSR1 | 16 | 280 |  | 239.4387 | 215.4948 | 5%
SSR2 | 35 | 1356.25 |  | 1949.5964 | 1754.6368 | 50%
Racks
HB650 | 12 | 60 |  | 7.2 | 7.2 | 50%
HWR | 4 | 7 |  | 2.4 | 2.4 | 5%
LB650 | 11 | 55 |  | 6.6 | 6.6 | 50%
SSR1 | 6 | 0 |  | 3.6 | 3.6 | 25%
SSR2 | 12 | 0 |  | 7.2 | 7.2 | 50%
Reflected Power Loads
HB650 | 36 | 0 |  | 0 | 0 | 5%
HWR | 8 | 0 |  | 0 | 0 | 5%
LB650 | 33 | 0 |  | 0 | 0 | 5%
SSR1 | 16 | 0 |  | 0 | 0 | 5%
SSR2 | 35 | 0 |  | 0 | 0 | 5%
Grand Total | 429 | 10120.75 |  | 13015.7183 | 11289.6479 | 20.62%

## Requirements Data
-> Enter only relevant fields for items that take up floor space, require environmental control, cooling water, AC power, a rack, or networking. -> If equipment does not extend beyond the rack it does not need to be included. Including cables will allow us to determine equipment location based on access to power or networking. -> If multiple cable types run to the same rack select the least flexible cable type going to the rack and provide the total number of all cables. -> Columns D-H have a "red triangle" in the right-hand corner -- hoover the mouse over them to view addtional information.
Room Data Sheet
|  | PIP-II | [60 empty] | C_
= Denotes missing information
= Data cells not applicable
[6 empty] | #N/A | = These cells are automatically calculated, no input required
|  |  | Start Here ↓ | [8 empty] | Design Uncertainty |  |  | Spatial Requirements |  |  |  |  | Floor Requirements |  |  | Environmental | [5 empty] | Cooling | [7 empty] | AC Distribution | [13 empty] | Racks |  |  |  | Cables |  |  | Safety |  |  | Communication
Identifier | WBS Level 2 | WBS ID | WBS Name | Building | Space Designation Location | Sub-System | User Defined Sub-System | Component | Description | Identifier - To Be Deleted | Quantity | Level of Design | Source of Requirements | Uncertainty Multiplier | Space Type | Length (in) | Width (in) | Height (in) | Weight (lbs) | Floor Flatness | Vibration | Finishes | Heating (F) | Cooling (F) | Humidity (%) | Pressurization Requirement | ODH (air changes/hr) | Any Special Ventilation (CFM) | Cooling Type | Heat Load (KW) | Total Heat Load (KW) | Heat Load to Air from Cables (KW) | Supply Nominal (F) | Supply Max (F) | Stability (F) | ΔT (F) | Power Requirement | Volts | Amps | Volt-Amperes | Total KVA | Power Factor (%) | Total Power (KW) | UPS (kVA / time (min)) | Standby Power (kVA) | Breaker (A) | Line Filter? | Dedicated Disconnect? | Special LOTO Provisions? | Special Grounding Required? | Size | Front Access | Closed Sides | Rear | Access to Power or Signal Cable Tray? | Cable Type | Count | Load greater than 50 V/100 A | Xrays? | ESS (Electrical Safety System) | Please select type of comm. | Notes/Other Requirements | Column1
DM-001 | 121.3 | 121.3.07 | Controls | LG | LG-BTL Power Supply | Computers, Front End |  | Racks | Networking, permits etc. |  | 3 | Preliminary | Off the Shelf | 5% | Floor | 30 | 24 | 60 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 0.5 | 1.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 10 | 1200 | 3.6 | 60 | 2.16 | NA | NA | 20 | Yes | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Closed | Yes | Flexible <1cm (e.g. RG58) | 2 | Yes | No | No | Ethernet | One rack requires two 120V-20A | C_Controls
DM-002 | 121.3 | 121.3.08 | SS | LG | LG-BTL Power Supply | Interlocks |  | Racks | ESS interface |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 30 | 24 | 36 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 0.3 | 0.3 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 7 | 840 | 0.84 | 20 | 0.168 | NA | NA | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left Only | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 2 | Yes | No | Yes | Other (specify) | Requires additional "End Rack". Connection to Safety System Network | C_SS
DM-003 | 121.3 | 121.3.06 | Vacuum | LG | LG-BTL Power Supply | Ion Pump PS System |  | Racks | Bulk, Ion pump PS, guage interface, network switch |  | 2 | Preliminary | Off the Shelf | 5% | Floor | 30 | 24 | 60 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 0.3 | 0.6 | [5 empty] | 208 V - 3 Phase - 3 Wire | 208 | 20 | 7205.3314 | 14.4107 | 30 | 4.3232 | NA | NA | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Open | Closed | Yes | Flexible <1cm (e.g. RG58) | 4 | Yes | No | No | Ethernet | Located near LCW PLC controls. Additional 120V 10A circuit for network switch | C_Vacuum
DM-004 | 121.3 | 121.3.09 | Instrumentation | LG | LG-BTL Power Supply | BPM |  | Racks | BPM, BLM, Profile Monitors |  | 3 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 60 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 0.5 | 1.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 20 | 2400 | 7.2 | 60 | 4.32 | NA | NA | 20 | Yes | No | No | No | 19"W/52U X 29" D | Open | Open | Closed | Yes | Flexible <1cm (e.g. RG58) | 320 | Yes | No | No | Ethernet |  | C_Instrumentation
DM-005 | 121.5 | 121.5.04 | BTLBAL | LG | LG-BTL Power Supply | Collimator Controls |  | Racks |  |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 30 | 24 | 60 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 0.3 | 0.3 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 20 | 2400 | 2.4 | 80 | 1.92 | NA | NA | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Open | Closed | Yes | Flexible <1cm (e.g. RG58) | 21 | Yes | No | No | ACNET |  | C_BTLBAL
DM-005.1 | 121.3 | 121.3.05 | Magnets | LG | LG-BTL Power Supply | Fast Dipole Switch |  | Racks | Pulse Magnet Power Supply |  | 1 | Conceptual | Expert Opinion | 50% | Floor | 30 | 24 | 60 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 0.1 | 0.1 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 20 | 16627.6878 | 16.6277 | 70 | 11.6394 | NA | NA | 20 | No | No | Yes | Yes | 19"W/60U X 29" D | Open | Left AND Right | Closed | Yes | "Flexible" >1cm (e.g. 500MCM stranded) | 8 | Yes | No | Yes | Ethernet |  | C_Magnets
DM-005.2 | 121.3 | 121.3.05 | Magnets | BTL | LG-BTL Power Supply | Fast Dipole Switch |  | Cables |  |  | 8 | Preliminary | Prototype-Testing | 25% | [14 empty] | Air, Environment |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | [12 empty] | "Flexible" >1cm (e.g. 500MCM stranded) | 8 | No | No | No |  |  | C_Magnets
DM-005.3 | 121.3 | 121.3.05 | Magnets | BTL | LG-BTL Power Supply | Fast Dipole Switch |  | Magnets |  |  | 1 | Conceptual | Expert Opinion | 50% | [14 empty] | Air, Environment |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | [14 empty] | No | No | No |  |  | C_Magnets
DM-006 | 121.3 | 121.3.05 | Magnets | LG | LG-BTL Power Supply | Magnets, Dipole |  | Power Supplies | 75KW Spange PS |  | 5 | Preliminary | Off the Shelf | 5% | Floor | 31.5 | 24 | 51 | 645 |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | LCW | 12 | 60 | 3 | 90 | 105 | 1 |  | 480 V - 3 Phase - 3 Wire | 480 | 125 | 103923.0485 | 519.6152 | 90 | 467.6537 | NA | NA | 125 | No | Yes | Yes | No | Other | Doors | Left AND Right | Closed | Yes | "Flexible" >1cm (e.g. 500MCM stranded) | 4 | Yes | No | Yes | Ethernet |  | C_Magnets
DM-007 | 121.3 | 121.3.05 | Magnets | Booster | Booster | Magnets, Dipole |  | Power Supplies | 125KW Spange PS |  | 2 | Preliminary | Off the Shelf | 5% | Floor | 31.5 | 24 | 51 | 645 |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | LCW | 20 | 40 | 5 | 90 | 105 | 1 |  | 480 V - 3 Phase - 3 Wire | 480 | 200 | 166276.8775 | 332.5538 | 90 | 299.2984 | NA | NA | 200 | No | Yes | Yes | No | Other | Doors | Left AND Right | Closed | Yes | "Flexible" >1cm (e.g. 500MCM stranded) | 8 | Yes | No | Yes | Ethernet |  | C_Magnets
DM-008 | 121.3 | 121.3.05 | Magnets | BTL | BTL-Beamline Tunnel | Magnets, Dipole |  | Cables | Dipole cables |  | 20 | Preliminary | Off the Shelf | 5% | [14 empty] | Air, Environment |  | 0 | 0.65 | [7 empty] | 0 | 0 | 100 | 0 | [11 empty] | Yes | "Flexible" >1cm (e.g. 500MCM stranded) | 20 | No | No |  |  | Cables for line #24Dipole PS | C_Magnets
DM-009 | 121.3 | 121.3.05 | Magnets | BTL | BTL-Beamline Tunnel | Magnets, Dipole |  | Cables | Dipole cables |  | 16 | Preliminary | Off the Shelf | 5% | [14 empty] | Air, Environment |  | 0 | 2.2 | [7 empty] | 0 | 0 | 100 | 0 | [11 empty] | Yes | "Flexible" >1cm (e.g. 500MCM stranded) | 16 | No | No |  |  | Cables for line #25 Dipole PS | C_Magnets
DM-010 | 121.3 | 121.3.05 | Magnets | LG | LG-BTL Power Supply | Magnets, Regular Quadrupole |  | Racks |  |  | 5 | Preliminary | Off the Shelf | 5% | Floor | 30 | 24 | 90 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 10 | 50 | [5 empty] | 480Y/277 V - 3 Phase - 4 Wire | 480 | 60 | 49883.0633 | 249.4153 | 100 | 249.4153 |  |  | 60 |  | Yes |  | No | 19"W/52U X 29" D | Open | Left AND Right | Closed | Yes | "Flexible" >1cm (e.g. 500MCM stranded) | 56 | Yes | No | Yes | Ethernet | Four 480V-60A circuits, two 208V-15A circuits, two 120V 20A circuits | C_Magnets
DM-011 | 121.3 | 121.3.05 | Magnets | BTL | BTL-Beamline Tunnel | Magnets, Regular Quadrupole |  | Cables | Quad Cables |  | 32 | Conceptual | Off the Shelf | 5% | [14 empty] | Air, Environment |  | 0 | 3.1 | [7 empty] | 0 | 0 | 100 | 0 | [13 empty] | 32 | No | No |  |  |  | C_Magnets
DM-012 | 121.3 | 121.3.05 | Magnets | BTL | BTL-Beamline Tunnel | Magnets, Regular Quadrupole |  | Magnets |  |  | 57 | Conceptual | Prototype-Testing | 25% | [7 empty] | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  |  | LCW | 0.53 | 30.21 | 2.5 | 90 | 105 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No | No |  |  |  | C_Magnets
DM-016 | 121.3 | 121.3.05 | Magnets | BTL | BTL-Beamline Tunnel | Magnets, Regular Quadrupole |  | Magnets | Booster inj. C Mag. |  | 1 | Preliminary | Prototype-Testing | 25% | [7 empty] | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  |  | LCW | 6.1 | 6.1 | 0.6 | 90 | 105 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_Magnets
DM-017 | 121.3 | 121.3.05 | Magnets | LG | LG-BTL Power Supply | Magnets, Dipole Corrector |  | Racks | CE Dipoles |  | 2 | Preliminary | Off the Shelf | 5% | Floor | 30 | 24 | 90 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  |  | Air, Environment | 2 | 4 | [5 empty] | 208 V - 3 Phase - 3 Wire | 208 | 40 | 14410.6627 | 28.8213 | 100 | 28.8213 |  |  | 40 |  | Yes |  | No |  |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 60 | Yes | No | No | Ethernet | One 208V-40A, Two 120V-20A | C_Magnets
DM-018 | 121.3 | 121.3.05 | Magnets | BTL | BTL-Beamline Tunnel | Magnets, Dipole Corrector |  | Cables |  |  | 56 | Preliminary | Off the Shelf | 5% | [14 empty] | Air, Environment |  | 0 | 3.6 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 56 | No | No |  |  |  | C_Magnets
DM-019 | 121.3 | 121.3.05 | Magnets | BTL | BTL-Beamline Tunnel | Magnets, Dipole Corrector |  | Magnets |  |  | 56 | Preliminary | Off the Shelf | 5% | [7 empty] | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  |  | Air, Environment | 0.1 | 5.6 | [8 empty] | 0 | 0 | 100 | 0 | [13 empty] | 56 | No | No |  |  |  | C_Magnets
DM-020 | 121.5 | 121.5.04 | BTLBAL | BTL | BAL-Beam Asborber Space | RAW Absorber |  | Pumps | Pumps |  | 1 | Preliminary | Prototype-Testing | 25% | [14 empty] | LCW | 75 | 75 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 5 | 4156.9219 | 4.1569 | 100 | 4.1569 |  |  |  |  | Yes | Yes | [8 empty] | Yes |  |  |  | 480V pump power | C_BTLBAL
DM-021 | 121.5 | 121.5.04 | BTLBAL | BTL | BAL-Beam Asborber Space | RAW Absorber |  | Racks | Controls |  | 1 | Preliminary | Prototype-Testing | 25% | [16 empty] | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 0.6 | 100 | 0.6 | [14 empty] | Yes |  |  |  | 120V control power | C_BTLBAL
DN-001 | 121.2 | 121.2.06 | CDS | LG | LG-General | General Data Acquisition |  | Racks | Rittal Cryo Control Racks |  | 34 | Preliminary | Prototype-Testing | 25% | Floor | 64 | 16 | 84 |  |  |  |  | 72 +/- 5 | 72 +/- 5 |  |  |  |  | Air, Environment | 0.1 | 3.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 16.32 | 100 | 16.32 |  |  | 20 | TBD | No | No | N/A | Other | Doors | Left AND Right | Closed | Yes | Flexible <1cm (e.g. RG58) | 3400 | Yes | No | No | Ethernet | Estimate established after Jamboree | C_CDS
DN-001A | 121.2 | 121.2.06 | CDS | LG | LG-General | General Data Acquisition |  | Racks | Control Racks for CDS |  | 25 | Pre-conceptual | Expert Opinion | 50% | Floor | 32 | 24 | 96 |  |  |  |  | 72 +/- 5 | 72 +/- 5 |  |  |  |  | Air, Environment | 1 | 25 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 208 | 15 | 5403.9985 | 135.1 | 100 | 135.1 |  |  | 20 | TBD | No | No | N/A | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 1000 | Yes | No | No | Ethernet | Still working with Cryo on the details of these racks | C_CDS
DN-002 | 121.3 | 121.3.07 | Controls | LG | LG-General | General Data Acquisition |  | Racks | needs distribution along gallery |  | 27 | Conceptual | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 9 | Air, Environment | 0.5 | 13.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 48.6 | 100 | 48.6 |  |  | 20 | Yes | No | No | TBD | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 200 | Yes | No | No | Ethernet | If VOIP phones then need UPS | C_Controls
DN-003 | 121.3 | 121.3.07 | Controls | LG | LG-General | Motor Controllers |  | Racks | needs distribution along gallery |  | 9 | Conceptual | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 9 | Air, Environment | 0.5 | 4.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 10 | 1200 | 10.8 | 100 | 10.8 |  |  | 20 | Yes | No | No | TBD | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 100 | Yes | No | No | Ethernet | Motor controllers need 2x20 amp breakers | C_Controls
DN-004 | 121.3 | 121.3.07 | Controls | HBB | HBB-Control Room | Timing System |  | Racks |  |  | 2 | Pre-conceptual | Expert Opinion | 50% | Floor | 32 | 24 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 9 | Air, Environment | 0.5 | 1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 3.6 | 100 | 3.6 |  |  | 20 | Yes | No | No | TBD | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 100 | Yes | No | No | Ethernet |  | C_Controls
DN-005 | 121.3 | 121.3.07 | Controls | PUB | PUB | PLC/LCW Controls |  | Racks | 1 Rittal rack per LCW system |  | 4 | Preliminary | Off the Shelf | 5% | Floor | 64 | 16 | 84 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 9 | Air, Environment | 0.5 | 2 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 2.4 | 100 | 2.4 |  |  | 20 | Yes | No | No | N/A | Other | Doors | Left AND Right | Closed |  | Flexible <1cm (e.g. RG58) | 100 | Yes | No | No | Ethernet | 1 rack per LCW system | C_Controls
DN-006 | 121.3 | 121.3.07 | Controls | BAL | BAL-Beam Asborber Space | RAW System |  | Racks | Rittal rack |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 64 | 16 | 84 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  |  | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 0.6 | 100 | 0.6 |  |  | 20 | Yes | No | No | N/A | Other | Doors | Left AND Right | Closed |  | Flexible <1cm (e.g. RG58) | 100 | Yes | No | No | Ethernet |  | C_Controls
DN-007 | 121.3 | 121.3.07 | Controls | HBB | HBB-Computer Space | Fiber Distribution |  | Racks |  |  | 3 | Conceptual | Off the Shelf | 5% | Floor | 32 | 24 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  |  | Air, Environment | 0.5 | 1.5 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 120 | 5 | 1039.2305 | 3.1177 | 100 | 3.1177 |  |  | 20 | Yes | No | No | TBD | 19"W/60U X 29" D | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 10 | Yes | No | No | Other (specify) | Feed through only no comm. needed | C_Controls
DN-008 | 121.3 | 121.3.07 | Controls | PUB | PUB | General Data Acquisition |  | Racks |  |  | 1 | Conceptual | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | Yes | No | No | TBD | 19"W/60U X 29" D | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 10 | Yes | No | No | Ethernet |  | C_Controls
DN-009 | 121.3 | 121.3.07 | Controls | CP | Cryoplant Building | General Data Acquisition |  | Racks |  |  | 1 | Conceptual | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | Yes | No | No | TBD | 19"W/60U X 29" D | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 10 | Yes | No | No | Ethernet |  | C_Controls
DN-010 | 121.3 | 121.3.07 | Controls | LG | LG-BTL Power Supply | General Data Acquisition |  | Racks |  |  | 6 | Conceptual | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 9 | Air, Environment | 0.5 | 3 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 10.8 | 100 | 10.8 |  |  | 20 | Yes | No | No | TBD | 19"W/60U X 29" D | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 10 | Yes | No | No | Ethernet |  | C_Controls
DN-011 | 121.3 | 121.3.07 | Controls | LG | LG-General | Computers, Console |  | Consoles, Fixed |  |  | 10 | Preliminary | Expert Opinion | 50% | Rack Mounted | 32 | 24 | 36 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  |  | Air, Environment | 0.05 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 4.8 | 100 | 4.8 |  |  | 20 | No | No | No | No | Other |  |  |  |  | Flexible <1cm (e.g. RG58) | 5 | Yes | No | No | ACNET, WIFI |  | C_Controls
DN-012 | 121.3 | 121.3.07 | Controls | LG | LG-General | Computers, Console |  | Consoles, Mobile |  |  | 10 | Preliminary | Expert Opinion | 50% | Floor | 32 | 24 | 36 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  |  | Air, Environment | 0.06 | 0.6 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 4.8 | 100 | 4.8 |  |  | 20 | No | No | No | No | Other |  |  |  |  | Flexible <1cm (e.g. RG58) | 5 | Yes | No | No | ACNET, WIFI |  | C_Controls
DN-013 | 121.3 | 121.3.07 | Controls | HBB | HBB-Control Room | Computers, Console |  | Consoles, Fixed |  |  | 3 | Preliminary | Expert Opinion | 50% | Floor | 32 | 24 | 36 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  |  | Air, Environment | 0.06 | 0.18 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 1.44 | 100 | 1.44 |  |  | 20 | No | No | No | No | Other |  |  |  |  | Flexible <1cm (e.g. RG58) | 6 | Yes | No | No | ACNET, WIFI |  | C_Controls
DN-014 | 121.3 | 121.3.03 | HPRF | LG | LG-HWR | HWR |  | Racks | HWR amplifiers are mounted in these racks along with PLC. HLA is represented here as well. |  | 4 | Final | Off the Shelf | 5% | Floor | [13 empty] | Air, Environment | 1.75 | 7 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 2.4 | 100 | 2.4 | [7 empty] | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Rigid (e.g. hardline coax) | 40 | Yes | No | Yes | ACNET | Suspect at most 2 in a rack Fewest # is 4 if only used for HPRF HWR-1 208 3phase 3 wire, HWR2-8 480 3phase 4 wire. | C_HPRF
DN-014.2 | 121.3 | 121.3.07 | Controls | LG | LG-General | General Data Acquisition | LCW/Vacumm controls readbacks |  |  |  | 13 | Preliminary | Expert Opinion | 50% | Floor | 64 | 16 | 84 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  |  | Air, Environment | 0.5 | 6.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 7.8 | 100 | 7.8 |  |  | 20 | Yes | No | No | N/A | Other | Doors | Left AND Right | Closed | Yes | Flexible <1cm (e.g. RG58) | 100 | Yes | No | No | Ethernet | Additonal Rittal racks for LCW/Vacuum
DN-014.1 | 121.3 | 121.3.07 | Controls | HBB | HBB-Lower High Bay | RFQ |  | Racks | PLC/LCW Controls - 1 Rittal rack per LCW system |  | 4 | Preliminary | Off the Shelf | 5% | Floor | 64 | 16 | 84 |  |  |  |  | 75 +/- 5 | 75 +/- 5 |  |  |  |  | Air, Environment | 0.5 | 2 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 2.4 | 100 | 2.4 |  |  | 20 | Yes | No | No | N/A | Other | Doors | Left AND Right | Closed | Yes | Flexible <1cm (e.g. RG58) | 100 | Yes | No | No | Ethernet | 1 rack per LCW system | C_Controls
DN-015 | 121.3 | 121.3.03 | HPRF | LG | LG-HWR | HWR |  | Power Amplifiers |  |  | 8 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 40-95F | 82 +/-4 |  |  |  |  | LCW | 15.75 | 126 |  | 86 | 90 | 4 |  | 480Y/277 V - 3 Phase - 4 Wire | 480 | 18 | 14964.919 | 119.7194 | 90 | 107.7474 |  | NA | 30 | No | Yes | No | No | Other | Open | Left AND Right | Closed | Yes | Rigid (e.g. hardline coax) | 10 | Yes | No | Yes | ACNET |  | C_HPRF
DN-016 | 121.3 | 121.3.03 | HPRF | LG | LG-HWR | HWR |  | Circulators |  |  | 8 | Preliminary | Off the Shelf | 5% | Suspended |  |  |  | 350 | [9 empty] | LCW | 0 | 0 |  | 86 | 90 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [13 empty] | 414 | No |  |  |  | Cable count is scaled via CMTS1, held here as placeholder | C_HPRF
DN-017 | 121.3 | 121.3.03 | HPRF | LG | LG-HWR | HWR |  | Reflected Power Loads |  |  | 8 | Preliminary | Off the Shelf | 5% | Suspended |  |  |  | 16 | [9 empty] | LCW | 0 | 0 |  | 86 | 90 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_HPRF
DN-018 | 121.3 | 121.3.03 | HPRF | LG | LG-SSR1 | SSR1 |  | Racks |  |  | 6 | Preliminary | Prototype-Testing | 25% | Floor | 24 | 32 | 96 | [10 empty] | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 3.6 | 100 | 3.6 | [7 empty] | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Rigid (e.g. hardline coax) | 40 | Yes | No | Yes | ACNET |  | C_HPRF
DN-019 | 121.3 | 121.3.03 | HPRF | LG | LG-SSR1 | SSR1 |  | Power Amplifiers |  |  | 16 | Final | Off the Shelf | 5% | Floor | [7 empty] | 40-95F | 82 +/-4 |  |  |  |  | LCW | 15.75 | 252 |  | 88 | 92 | 4 | 7.1 | 480Y/277 V - 3 Phase - 4 Wire | 480 | 18 | 14964.919 | 239.4387 | 90 | 215.4948 |  | NA | 40 | No | Yes | No | No | Other | Open | Left AND Right | Closed | Yes | Rigid (e.g. hardline coax) | 10 | Yes | No | Yes | ACNET |  | C_HPRF
DN-019.1 | 121.3 | 121.3.03 | HPRF | LG | LG-SSR1 | SSR1 |  | Power Amplifiers | HLA for SSR1 |  | 0 | Final | Off the Shelf | 5% | [14 empty] | Air, Environment | 1.75 | 28 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_HPRF
DN-020 | 121.3 | 121.3.03 | HPRF | LG | LG-SSR1 | SSR1 |  | Circulators |  |  | 16 | Preliminary | Off the Shelf | 5% | Suspended |  |  |  | 350 | [9 empty] | LCW | 0 | 0 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [13 empty] | 658 | No |  |  |  | Cable count is scaled via CMTS1, held here as placeholder | C_HPRF
DN-021 | 121.3 | 121.3.03 | HPRF | LG | LG-SSR1 | SSR1 |  | Reflected Power Loads |  |  | 16 | Preliminary | Off the Shelf | 5% | Suspended |  |  |  | 16 | [9 empty] | LCW | 0 | 0 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_HPRF
DN-022 | 121.3 | 121.3.03 | HPRF | LG | LG-SSR2 | SSR2 |  | Racks | Control equipment rack for PLCs |  | 12 | Preliminary | Expert Opinion | 50% | Floor | [13 empty] | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 7.2 | 100 | 7.2 | [7 empty] | 19"W/60U X 29" D | Doors | Left AND Right | Door | Yes | Rigid (e.g. hardline coax) | 40 | Yes | No | Yes | ACNET |  | C_HPRF
DN-023 | 121.3 | 121.3.03 | HPRF | LG | LG-SSR2 | SSR2 |  | Power Amplifiers |  |  | 35 | Conceptual | Expert Opinion | 50% | Floor | 72 | 48 | 96 |  |  |  |  | 40-95F | 82 +/-4 |  |  |  |  | LCW | 33.75 | 1181.25 |  | 88 | 92 | 4 | 8.1 | 480Y/277 V - 3 Phase - 4 Wire | 480 | 67 | 55702.754 | 1949.5964 | 90 | 1754.6368 |  | NA | 120 | No | Yes | No | No | Other | Open | Left AND Right | Closed | Yes | Rigid (e.g. hardline coax) | 10 | Yes | No | Yes | ACNET |  | C_HPRF
DN-023.1 | 121.3 | 121.3.03 | HPRF | LG | LG-SSR2 | SSR2 |  | Power Amplifiers | HLA for SSR2 |  | 0 | Conceptual | Expert Opinion | 50% | [14 empty] | Air, Environment | 5 | 175 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | This item is only for the HLA component of the power amplifiers | C_HPRF
DN-024 | 121.3 | 121.3.03 | HPRF | LG | LG-SSR2 | SSR2 |  | Circulators |  |  | 35 | Preliminary | Off the Shelf | 5% | Suspended |  |  |  | 350 | [9 empty] | LCW | 0 | 0 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [13 empty] | 2113 | No |  |  |  | Cable count is scaled via CMTS1, held here as placeholder | C_HPRF
DN-025 | 121.3 | 121.3.03 | HPRF | LG | LG-SSR2 | SSR2 |  | Reflected Power Loads |  |  | 35 | Preliminary | Off the Shelf | 5% | Suspended |  |  |  | 16 | [9 empty] | LCW | 0 | 0 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_HPRF
DN-026 | 121.3 | 121.3.03 | HPRF | LG | LG-LB650 | LB650 |  | Racks | Control equipment rack for PLCs |  | 11 | Preliminary | Expert Opinion | 50% | Floor | [13 empty] | Air, Environment | 5 | 55 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 6.6 | 100 | 6.6 | [7 empty] | 19"W/60U X 29" D | Doors | Left AND Right | Door | Yes | Rigid (e.g. hardline coax) | 40 | Yes | No | Yes | ACNET |  | C_HPRF
DN-027 | 121.3 | 121.3.03 | HPRF | LG | LG-LB650 | LB650 |  | Power Amplifiers | 40 kW |  | 33 | Preliminary | Expert Opinion | 50% | Floor | 72 | 134 | 96 |  |  |  |  | 40-95F | 82 +/-4 | na |  |  |  | LCW | 85.5 | 2821.5 |  | 88 | 92 | 4 | 7.2 | 480Y/277 V - 3 Phase - 4 Wire | 480 | 134 | 111405.5079 | 3676.3818 | 86 | 3161.6883 |  | NA | 240 | No | Yes | No | No | Other | Open | Left AND Right | Closed | Yes | Rigid (e.g. hardline coax) | 10 | Yes | No | Yes | ACNET |  | C_HPRF
DN-027.1 | 121.3 | 121.3.03 | HPRF | LG | LG-LB650 | LB650 |  | Power Amplifiers | HLA for 40 kW |  | 0 | Pre-conceptual | Prototype-Testing | 25% | [14 empty] | Air, Environment | 10 | 330 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | This item is only for the HLA component of the power amplifiers | C_HPRF
DN-028 | 121.3 | 121.3.03 | HPRF | LG | LG-LB650 | LB650 |  | Circulators |  |  | 33 | Preliminary | Off the Shelf | 5% | Suspended |  |  |  | 350 | [9 empty] | LCW | 0 | 0 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [13 empty] | 3118 | No |  |  |  | Cable count is scaled via CMTS1, held here as placeholder | C_HPRF
DN-029 | 121.3 | 121.3.03 | HPRF | LG | LG-LB650 | LB650 |  | Reflected Power Loads |  |  | 33 | Preliminary | Off the Shelf | 5% | Suspended |  |  |  | 17 | [9 empty] | LCW | 0 | 0 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_HPRF
DN-030 | 121.3 | 121.3.03 | HPRF | LG | LG-HB650 | HB650 |  | Racks | Control equipment rack for PLCs |  | 12 | Preliminary | Expert Opinion | 50% | Floor | [13 empty] | Air, Environment | 5 | 60 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 7.2 | 100 | 7.2 | [7 empty] | 19"W/60U X 29" D | Doors | Left AND Right | Door | Yes | Rigid (e.g. hardline coax) | 40 | Yes | No | Yes | ACNET |  | C_HPRF
DN-031 | 121.3 | 121.3.03 | HPRF | LG | LG-HB650 | HB650 |  | Power Amplifiers | 70 kW |  | 36 | Preliminary | Expert Opinion | 50% | Floor | 96 | 134 | 96 |  |  |  |  | 40-95F | 82 +/-4 |  |  |  |  | LCW | 123.75 | 4455 |  | 88 | 92 | 4 | 7.2 | 480Y/277 V - 3 Phase - 4 Wire | 480 | 234 | 194543.9467 | 7003.5821 | 86 | 6023.0806 |  | NA | 450 | No | Yes | No | No | Other | Open | Left AND Right | Closed | Yes | Rigid (e.g. hardline coax) | 10 | Yes | No | Yes | ACNET |  | C_HPRF
DN-031.1 | 121.3 | 121.3.03 | HPRF | LG | LG-HB650 | HB650 |  | Power Amplifiers | HLA for 70 kW |  | 0 | Pre-conceptual | Prototype-Testing | 25% | [14 empty] | Air, Environment | 17.5 | 630 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | This item is only for the HLA component of the power amplifiers | C_HPRF
DN-032 | 121.3 | 121.3.03 | HPRF | LG | LG-HB650 | HB650 |  | Circulators |  |  | 36 | Preliminary | Off the Shelf | 5% | Suspended |  |  |  | 350 | [9 empty] | LCW | 0 | 0 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [13 empty] | 1240 | No |  |  |  | Cable count is scaled via CMTS1, held here as placeholder | C_HPRF
DN-033 | 121.3 | 121.3.03 | HPRF | LG | LG-HB650 | HB650 |  | Reflected Power Loads |  |  | 36 | Preliminary | Off the Shelf | 5% | Suspended |  |  |  | 17 | [9 empty] | LCW | 0 | 0 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_HPRF
DN-034 | 121.3 | 121.3.09 | Instrumentation | HBB | HBB-Upper High Bay | General Instrumentation |  | Racks | WFE |  | 5 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 2.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 13 | 1560 | 7.8 | 100 | 7.8 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 20 | Yes | No | No | Ethernet | Currently 4 at PIP2IT but they are filling | C_Instrumentation
DN-035 | 121.3 | 121.3.09 | Instrumentation | LG | LG-HWR, LG-SSR1, LG-SSR2 | General Instrumentation |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 13 | 1560 | 1.56 | 100 | 1.56 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 20 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-036 | 121.3 | 121.3.09 | Instrumentation | LG | LG-HWR, LG-SSR1, LG-SSR2 | BPM |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 3 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 1.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 5.76 | 100 | 5.76 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 172 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-037 | 121.3 | 121.3.09 | Instrumentation | LG | LG-HWR, LG-SSR1, LG-SSR2 | BLM |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 1.92 | 100 | 1.92 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 186 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-038 | 121.3 | 121.3.09 | Instrumentation | LG | LG-HWR, LG-SSR1, LG-SSR2 | MW, Laser Wire |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 2 | Preliminary | Expert Opinion | 50% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 13 | 1560 | 3.12 | 100 | 3.12 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 20 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-039 | 121.3 | 121.3.09 | Instrumentation | LG | LG-LB650, LG-HB650 | General Instrumentation |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 13 | 1560 | 1.56 | 100 | 1.56 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 20 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-040 | 121.3 | 121.3.09 | Instrumentation | LG | LG-LB650, LG-HB650 | BPM |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 3 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 1.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 5.76 | 100 | 5.76 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 172 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-041 | 121.3 | 121.3.09 | Instrumentation | LG | LG-LB650, LG-HB650 | BLM |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 1.92 | 100 | 1.92 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 186 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-042 | 121.3 | 121.3.09 | Instrumentation | LG | LG-LB650, LG-HB650 | MW, Laser Wire |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 2 | Preliminary | Expert Opinion | 50% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 13 | 1560 | 3.12 | 100 | 3.12 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 20 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-043 | 121.3 | 121.3.09 | Instrumentation | LG | LG-BTL Power Supply | General Instrumentation |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 13 | 1560 | 1.56 | 100 | 1.56 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 20 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-044 | 121.3 | 121.3.09 | Instrumentation | LG | LG-BTL Power Supply | BPM |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 3 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 1.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 5.76 | 100 | 5.76 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 172 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-045 | 121.3 | 121.3.09 | Instrumentation | LG | LG-BTL Power Supply | BLM |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 2 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 3.84 | 100 | 3.84 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 186 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-045.1 | 121.3 | 121.3.09 | Instrumentation | HBB | HBB-Lower High Bay | Laser Wire |  | Laser Room | Primary Laser Rm |  | 1 | Preliminary | Expert Opinion | 50% | Floor | 216 | 180 | 96 |  |  |  |  | 75 +/-3 | 75 +/-3 |  |  |  |  | Air, Environment |  | 0 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 208 | 15 | 5403.9985 | 5.404 | 100 | 5.404 | [7 empty] | Other | [6 empty] | Yes |  |  |  | Laser Rooms parameters are unknown | C_Instrumentation
DN-045.2 | 121.3 | 121.3.09 | Instrumentation | LT | LT-HB650 | Laser Wire |  | Laser Room | Secondary Laser Rm |  | 1 | Preliminary | Expert Opinion | 50% | Floor | 216 | 180 | 96 |  |  |  |  | 75 +/-3 | 75 +/-3 | [6 empty] | 0 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 208 | 15 | 5403.9985 | 5.404 | 100 | 5.404 | [7 empty] | Other | [6 empty] | Yes |  |  |  | Laser Rooms parameters are unknown | C_Instrumentation
DN-046 | 121.3 | 121.3.09 | Instrumentation | LG | LG-BTL Power Supply | Wire Scanner |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 2 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 3.84 | 100 | 3.84 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 40 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-047 | 121.3 | 121.3.04 | LLRF | HBB | HBB-Upper High Bay | Primary Reference Line |  |  | MO/PRL - 4x4x1 MO+ 36U rack |  | 1 | Final | Prototype-Testing | 30% | Floor, Suspended | 84 | 48 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0.42 | 100 | 0.42 | .4/120 | 0.4 | 20 | Yes |  |  |  | Other | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 16 | Yes | N/A | N/A | ACNET | Wall Mounted Tunnel side @ beginning of frequecy section. Direct access to tunnel (penetration) | C_LLRF
DN-048 | 121.3 | 121.3.04 | LLRF | HBB | HBB-Upper High Bay | RFQ |  | Racks | 162.5-1.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | Yes | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 7 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-049 | 121.3 | 121.3.04 | LLRF | HBB | HBB-Upper High Bay | Buncher |  | Racks | 162.5-1.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | Yes | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 15 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-050 | 121.3 | 121.3.04 | LLRF | HBB | HBB-Upper High Bay | HWR |  | Racks | 162.5-1.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | Yes | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 20 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-051 | 121.3 | 121.3.04 | LLRF | HBB | HBB-Upper High Bay | HWR |  | Racks | 162.5-1.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | Yes | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 20 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-052 | 121.3 | 121.3.04 | LLRF | HBB | HBB-Upper High Bay | RF Interlocks |  | Racks | 162.5-1.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | Yes | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 5 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-053 | 121.3 | 121.3.04 | LLRF | HBB | HBB-Upper High Bay | RF Interlocks |  | Racks | 162.5-1.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | Yes | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 71 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-054 | 121.3 | 121.3.04 | LLRF | HBB | HBB-Upper High Bay | RFQ, Buncher, HWR | Combination of all 6 racks for RFQ/Buncher/HWR. Captured here for floor space a positioning purposes. | 162.5 LLRF Hardware | 162.5 Station 1 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [14 empty] | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-055 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR1 | SSR1 |  | Resonance Control | MO/PRL - 4x4x1 MO+ 36U rack |  | 1 | Final | Prototype-Testing | 30% | Floor, Suspended | 84 | 48 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0.4 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0.42 | 100 | 0.42 | .4/120 | 0.4 | [5 empty] | Other | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 16 | Yes | N/A | N/A | ACNET | Wall Mounted Tunnel side @ beginning of frequecy section | C_LLRF
DN-056 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR1 | SSR1 |  | Racks | 325-1.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-057 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR1 | SSR1 |  | Racks | 325-1.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 27 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-058 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR1 | SSR1 |  | Racks | 325-1.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-059 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR1 | RF Interlocks |  | Racks | 325-1.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-060 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR1 | RF Interlocks |  | Racks | 325-1.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 87 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-061 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR1 | Spare |  | Racks | 325-1.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 112 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-062 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | SSR1 | Combination of all 6 racks for SSR station 1. Captured here for floor space a positioning purposes. | 325 LLRF Hardware | 325 Station 1 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-063 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-2.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-064 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-2.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 27 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-065 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-2.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-066 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | RF Interlocks |  | Racks | 325-2.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 154 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-067 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | RF Interlocks |  | Racks | 325-2.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-068 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | Spare |  | Racks | 325-2.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-069 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | SSR2 | Combination of all 6 racks for SSR station 2. Captured here for floor space a positioning purposes. | 325 LLRF Hardware | 325 Station 2 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-070 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-3.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-071 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-3.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 27 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-072 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-3.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-073 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | RF Interlocks |  | Racks | 325-3.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 157 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-074 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | RF Interlocks |  | Racks | 325-3.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-075 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | Spare |  | Racks | 325-3.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-076 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | SSR2 | Combination of all 6 racks for SSR station 3. Captured here for floor space a positioning purposes. | 325 LLRF Hardware | 325 Station 3 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-077 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-4.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-078 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-4.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 27 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-079 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-4.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 18 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-080 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | RF Interlocks |  | Racks | 325-4.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 138 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-081 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | RF Interlocks |  | Racks | 325-4.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-082 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | Spare |  | Racks | 325-4.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-083 | 121.3 | 121.3.04 | LLRF | LG | LG-SSR2 | SSR2 | Combination of all 6 racks for SSR station 4. Captured here for floor space a positioning purposes. | 325 LLRF Hardware | 325 Station 4 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-084 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | LB650 |  | Resonance Control | MO/PRL - 4x4x1 MO+ 36U rack |  | 1 | Final | Prototype-Testing | 30% | Floor, Suspended | 84 | 48 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0.4 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0.42 | 100 | 0.42 | .4/120 | 0.4 | [5 empty] | Other | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 16 | Yes | N/A | N/A | ACNET | Wall Mounted Tunnel side @ beginning of frequecy section | C_LLRF
DN-085 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-1.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 20 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-086 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-1.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 22 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-087 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-1.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 23 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-088 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | RF Interlocks |  | Racks | 650-1.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 153 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-089 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | RF Interlocks |  | Racks | 650-1.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-090 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | Spare |  | Racks | 650-1.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-091 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | LB650 | Combination of all 6 racks for 650 station 1. Captured here for floor space a positioning purposes. | 650 LLRF Hardware | 650 Station 1 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-092 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-2.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-093 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-2.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 26 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-094 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-2.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-095 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | RF Interlocks |  | Racks | 650-2.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 154 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-096 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | RF Interlocks |  | Racks | 650-2.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-097 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | Spare |  | Racks | 650-2.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-098 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | LB650 | Combination of all 6 racks for 650 station 2. Captured here for floor space a positioning purposes. | 650 LLRF Hardware | 650 Station 2 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-099 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-3.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-100 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-3.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-101 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-3.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 6 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-102 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | RF Interlocks |  | Racks | 650-3.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 116 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-103 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | RF Interlocks |  | Racks | 650-3.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-104 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | Spare |  | Racks | 650-3.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-105 | 121.3 | 121.3.04 | LLRF | LG | LG-LB650 | LB650 | Combination of all 6 racks for 650 station 3. Captured here for floor space a positioning purposes. | 650 LLRF Hardware | 650 Station 3 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO, Need 3ft on all sides for access. | C_LLRF
DN-106 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | HB650 |  | Racks | 650-4.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-107 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | HB650 |  | Racks | 650-4.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 26 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-108 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | HB650 |  | Racks | 650-4.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-109 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | RF Interlocks |  | Racks | 650-4.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 144 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-110 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | RF Interlocks |  | Racks | 650-4.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-111 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | Spare |  | Racks | 650-4.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-112 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | LB650 | Combination of all 6 racks for 650 station 4. Captured here for floor space a positioning purposes. | 650 LLRF Hardware | 650 Station 4 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO | C_LLRF
DN-113 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | HB650 |  | Racks | 650-5.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-114 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | HB650 |  | Racks | 650-5.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 26 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-115 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | HB650 |  | Racks | 650-5.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-116 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | RF Interlocks |  | Racks | 650-5.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 144 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-117 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | RF Interlocks |  | Racks | 650-5.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-118 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | Spare |  | Racks | 650-5.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-119 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | HB650 | Combination of all 6 racks for 650 station 5. Captured here for floor space a positioning purposes. | 650 LLRF Hardware | 650 Station 5 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-120 | 121.3 | 121.3.04 | LLRF | LG | LG-HB650 | HB650 |  | Resonance Control | 650 MO amp - 36U rack |  | 1 | Final | Prototype-Testing | 30% | Floor | 60 | 66 | 48 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0.4 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0.42 | 100 | 0.42 | [7 empty] | Other | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 16 | Yes | N/A | N/A | ACNET | End of frequency section | C_LLRF
DN-121 | 121.3 | 121.3.05 | Magnets | LG | LG-HWR | Magnets, Dipole Corrector , Solenoids |  | Racks | switchers, 4QPM, bulk |  | 2 | Final | Off the Shelf | 15% | Floor | 32 | 24 | 96 |  |  | No |  | 78 +/-5 | 78 +/-5 | 55 |  |  | 900 | Air, Environment | 4.5 | 9 | 0.8 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 208 | 103.4 | 37251.5631 | 74.5031 | 86 | 64.0727 | yes | [6 empty] | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 82 | Yes | No | Yes | Ethernet | 208/120 modification (UPS as well) | C_Magnets
DN-122 | 121.3 | 121.3.05 | Magnets | LG | LG-HWR | Solenoids |  | Power Supplies |  |  | 8 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 0.5 | [7 empty] | 0 | 0 | 86 | 0 | na | 2.4 | 20 | Yes | Yes | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 32 | No | No | Yes |  |  | C_Magnets
DN-123 | 121.3 | 121.3.05 | Magnets | LG | LG-HWR | Magnets, Dipole Corrector |  | Power Supplies |  |  | 16 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 0.04 | [7 empty] | 0 | 0 | 86 | 0 | na | 2.4 | 20 | Yes | Yes | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 50 | No | No | Yes |  |  | C_Magnets
DN-124 | 121.3 | 121.3.05 | Magnets | LT | LT-HWR | Solenoids |  | Element/magnet |  |  | 8 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 0.5 | [7 empty] | 0 | 0 | 100 | 0 | [13 empty] | 16 | No |  |  |  |  | C_Magnets
DN-125 | 121.3 | 121.3.05 | Magnets | LT | LT-HWR | Magnets, Dipole Corrector |  | Element/magnet |  |  | 16 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 0.8 | [7 empty] | 0 | 0 | 100 | 0 | [13 empty] | 32 | No |  |  |  |  | C_Magnets
DN-126 | 121.3 | 121.3.05 | Magnets | LG | LG-SSR1 | Magnets, Dipole Corrector , Solenoids |  | Racks | switchers, 8QPM, bulk |  | 4 | Final | Off the Shelf | 5% | Floor | 32 | 24 | 96 |  |  | No |  | 78 +/-5 | 78 +/-5 | 55 |  |  | 900 | Air, Environment | 1.62 | 6.48 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 208 | 103.4 | 37251.5631 | 149.0063 | 86 | 128.1454 | yes | [6 empty] | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 148 | Yes | No | Yes | Ethernet | 208/120 modification (UPS as well) | C_Magnets
DN-127 | 121.3 | 121.3.05 | Magnets | LG | LG-SSR1 | Solenoids |  | Power Supplies |  |  | 8 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 0.5 | [7 empty] | 0 | 0 | 86 | 0 | na | 2.4 | 20 | Yes | Yes | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 42 | No | No | Yes |  |  | C_Magnets
DN-128 | 121.3 | 121.3.05 | Magnets | LG | LG-SSR1 | Magnets, Dipole Corrector |  | Power Supplies |  |  | 32 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 6.6 | [7 empty] | 0 | 0 | 86 | 0 | na | 2.4 | 20 | Yes | Yes | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 106 | No | No | Yes |  |  | C_Magnets
DN-129 | 121.3 | 121.3.05 | Magnets | LT | LT-SSR1 | Solenoids |  | Magnets |  |  | 8 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 0.5 | [7 empty] | 0 | 0 |  | 0 | [13 empty] | 16 | No |  |  |  |  | C_Magnets
DN-130 | 121.3 | 121.3.05 | Magnets | LT | LT-SSR1 | Magnets, Dipole Corrector |  | Magnets |  |  | 32 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 1.6 | [7 empty] | 0 | 0 |  | 0 | [13 empty] | 64 | No |  |  |  |  | C_Magnets
DN-131 | 121.3 | 121.3.05 | Magnets | LG | LG-SSR2 | Magnets, Dipole Corrector , Solenoids |  | Racks | 208/120 rack |  | 13 | Final | Off the Shelf | 5% | Floor | 32 | 24 | 96 |  |  | No |  | 78 +/-5 | 78 +/-5 | 55 |  |  | 900 | Air, Environment | 1.5 | 19.5 | 18 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 208 | 103.4 | 37251.5631 | 484.2703 | 86 | 416.4725 | yes | [6 empty] | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 392 | Yes | No | Yes | Ethernet | 208/120 modification (UPS as well) | C_Magnets
DN-132 | 121.3 | 121.3.05 | Magnets | LG | LG-SSR2 | Solenoids |  | Power Supplies |  |  | 21 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 1.5 | [7 empty] | 0 | 0 | 86 | 0 | na | 2.4 | 20 | Yes | Yes | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 112 | No | No | Yes |  |  | C_Magnets
DN-133 | 121.3 | 121.3.05 | Magnets | LG | LG-SSR2 | Magnets, Dipole Corrector |  | Power Supplies |  |  | 84 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 4.2 | [7 empty] | 0 | 0 | 86 | 0 | na | 2.4 | 20 | Yes | Yes | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 280 | No | No | Yes |  |  | C_Magnets
DN-134 | 121.3 | 121.3.05 | Magnets | LT | LT-SSR2 | Solenoids |  | Magnets |  |  | 21 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 1.5 | [7 empty] | 0 | 0 |  | 0 | [13 empty] | 42 | No |  |  |  |  | C_Magnets
DN-135 | 121.3 | 121.3.05 | Magnets | LT | LT-SSR2 | Magnets, Dipole Corrector |  | Magnets |  |  | 84 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 22.2 | [7 empty] | 0 | 0 |  | 0 | [13 empty] | 168 | No |  |  |  |  | C_Magnets
DN-136 | 121.3 | 121.3.05 | Magnets | LG | LG-LB650, LG-HB650 | Magnets, Regular Quadrupole |  | Racks | 1.5kW supplies, 84% efficient, 8/RR + Controller/regulators |  | 6 | Final | Off the Shelf | 15% | Floor | 32 | 24 | 96 |  |  | No |  | 78 +/-5 | 78 +/-5 | 55 |  |  | 900 | Air, Environment | 5.7 | 34.2 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 208 | 65.4 | 23561.4335 | 141.3686 | 86 | 121.577 | [7 empty] | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 143 | Yes | No | Yes | Ethernet |  | C_Magnets
DN-137 | 121.3 | 121.3.05 | Magnets | LG | LG-LB650, LG-HB650 | Magnets, Regular Quadrupole |  | Power Supplies |  |  | 44 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 3.5 | [7 empty] | 0 | 0 | 84 | 0 | NA | NA | 15 | TBD | TBD | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 143 | No | No | Yes | Ethernet | 208 circuit at 27.4 amp & 110 circuit at 38 amps | C_Magnets
DN-138 | 121.3 | 121.3.05 | Magnets | LG | LG-LB650, LG-HB650 | Magnets, Dipole Corrector |  | Racks | switchers,bulk |  | 2 | Final | Off the Shelf | 15% | Floor | 32 | 24 | 96 |  |  | No |  | 78 +/-5 | 78 +/-5 | 55 |  |  | 900 | Air, Environment | 1.2 | 2.4 | [5 empty] | 480Y/277 V - 3 Phase - 4 Wire | 480 | 28.34 | 23561.4335 | 47.1229 | 86 | 40.5257 |  |  | 40 |  |  |  |  | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 83 | Yes | No | Yes | Ethernet |  | C_Magnets
DN-139 | 121.3 | 121.3.05 | Magnets | LG | LG-LB650, LG-HB650 | Magnets, Dipole Corrector |  | Power Supplies |  |  | 40 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 0.04 | [7 empty] | 0 | 0 | 86 | 0 | NA | NA |  | TBD | TBD | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 80 | No | No | Yes | Ethernet | 208 circuit at 27.4 amp & 110 circuit at 38 amps | C_Magnets
DN-140 | 121.3 | 121.3.05 | Magnets | LT | LT-LB650, LT-HB650 | Magnets, Regular Quadrupole |  | Magnets |  |  | 44 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 |  |  |  | LCW | 0.5 | 22 | 3.5 | [7 empty] | 0 | 0 | 100 | 0 | [13 empty] | 88 | No |  |  |  |  | C_Magnets
DN-141 | 121.3 | 121.3.05 | Magnets | LT | LT-LB650, LT-HB650 | Magnets, Dipole Corrector |  | Magnets |  |  | 40 | Final | Off the Shelf | 15% |  | 118 | [6 empty] | 78 +/-5 | 78 +/-5 | 55 |  |  |  | Air, Environment | 0.04 | 1.6 | 0.4 | [7 empty] | 0 | 0 | 100 | 0 | [13 empty] | 80 | No |  |  |  |  | C_Magnets
DN-142 | 121.3 | 121.3.08 | SS | HBB | HBB-Control Room | Interlocks |  | Racks | CDC RMSS |  | 1 | Final | Off the Shelf | 15% | Floor | 30 | 32 | 96 |  |  | No |  | 72 +/- 5 | 72 +/- 5 | 55 |  |  |  | Air, Environment | 3.6 | 3.6 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 7 | 840 | 0.84 | 100 | 0.84 | internal (provided by SS) |  | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) |  | Yes | No | No | Ethernet | Must have an end rack 8" x 30" | C_SS
DN-143 | 121.3 | 121.3.08 | SS | LG | LG-SSR2, LG-LB650 | ODH |  | Racks | ODH |  | 1 | Final | Off the Shelf | 15% | Floor | 30 | 32 | 96 |  |  | No |  | 72 +/- 5 | 72 +/- 5 | 55 |  |  |  | Air, Environment | 2 | 2 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 7 | 840 | 0.84 | 100 | 0.84 | internal (provided by SS) |  | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Open | Yes | Flexible <1cm (e.g. RG58) |  | Yes | No | No | Ethernet | Must have an end rack 8" x 30" | C_SS
DN-144 | 121.3 | 121.3.08 | SS | LG | LG-HB650 | Interlocks |  | Racks | CDC RMSS |  | 1 | Final | Off the Shelf | 15% | Floor | 30 | 32 | 96 |  |  | No |  | 72 +/- 5 | 72 +/- 5 | 55 |  |  |  | Air, Environment | 3.6 | 3.6 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 7 | 840 | 0.84 | 100 | 0.84 | internal (provided by SS) |  | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Open | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) |  | Yes | No | No | Ethernet | Must have an end rack 8" x 30" | C_SS
DN-145 | 121.3 | 121.3.08 | SS | LG | LG-General | Interlocks, SSIU |  | Rack Mount | 2U rack mount |  | 22 | Final | Off the Shelf | 15% | Rack Mounted | 20 | 19 | 3 |  |  | No |  | 72 +/- 5 | 72 +/- 5 | 55 |  |  |  | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3 | 360 | 7.92 | 100 | 7.92 |  |  |  | No | No | No | No | Other |  |  |  |  | Flexible <1cm (e.g. RG58) |  | Yes | No | No | Ethernet | These SSIU units will just share rack space in other racks. | C_SS
DN-145.1 | 121.3 | 121.3.08 | SS | LG | LG-SSR1 | Interlocks |  | Interlock Box | Wall Mounted |  | 1 | Final | Off the Shelf | 5% | Suspended | 30 | 8 | 20 | [10 empty] | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3 | 360 | 0.36 | 100 | 0.36 | [14 empty] | Yes |  |  |  |  | C_SS
DN-145.2 | 121.3 | 121.3.08 | SS | LG | LG-BTL Power Supply | Interlocks |  | Interlock Box | Wall Mounted |  | 1 | Final | Off the Shelf | 5% | Suspended | 30 | 8 | 20 | [10 empty] | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3 | 360 | 0.36 | 100 | 0.36 | [14 empty] | Yes |  |  |  |  | C_SS
DN-146 | 121.3 | 121.3.06 | Vacuum | LT | LT-HWR, LT-SSR1, LT-SSR2 | HWR |  | Pump, Ion | HWR-SSR |  | 9 | Final | Off the Shelf | 15% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.9 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 9 | No |  |  |  | powered through controller | C_Vacuum
DN-147 | 121.3 | 121.3.06 | Vacuum | LG | LG-HWR, LG-SSR1, LG-SSR2 | HWR |  | Controller, Ion Pump | HWR-SSR |  | 9 | Final | Off the Shelf | 15% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.9 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.13094 | 100 | 0.13094 | [12 empty] | Flexible <1cm (e.g. RG58) | 9 | No |  |  |  |  | C_Vacuum
DN-148 | 121.3 | 121.3.06 | Vacuum | LT | LT-HWR | HWR |  | Gauges, Ion | HWR-SSR |  | 9 | Final | Off the Shelf | 15% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.9 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 9 | No |  |  |  | powered through controller | C_Vacuum
DN-149 | 121.3 | 121.3.06 | Vacuum | LT | LT-HWR | HWR |  | Gauges, Pirani | HWR-SSR |  | 9 | Final | Off the Shelf | 15% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.9 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 9 | No |  |  |  | powered through controller | C_Vacuum
DN-150 | 121.3 | 121.3.06 | Vacuum | LT | LT-HWR | HWR |  | Controller, Ion/Pirani Gauge | HWR-SSR |  | 18 | Final | Off the Shelf | 15% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 1.8 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 1.08 | 100 | 1.08 | [12 empty] | Flexible <1cm (e.g. RG58) | 18 | Yes |  |  |  |  | C_Vacuum
DN-151 | 121.3 | 121.3.06 | Vacuum | LG | LG-HWR | HWR |  | Racks | HWR-SSR |  | 1 | Final | Off the Shelf | 15% | Floor | 24 | 32 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | 0.5 | [7 empty] | 0 | 0 | 100 | 0 | [7 empty] | 19"W/52U X 29" D | Open | Left AND Right |  | Yes |  | 2 | No |  |  | Ethernet | Additional 120V 10A circuit for network switch | C_Vacuum
DN-152 | 121.3 | 121.3.06 | Vacuum | LT | LT-HWR, LT-SSR1, LT-SSR2 | HWR |  | Gate Valves | HWR-SSR |  | 20 | Final | Off the Shelf | 15% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.72 | 100 | 0.72 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-153 | 121.3 | 121.3.06 | Vacuum | LT | LT-LB650, LT-HB650 | SRF |  | Pump, Ion | SRF Warm units |  | 20 | Final | Off the Shelf | 15% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 2 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-154 | 121.3 | 121.3.06 | Vacuum | LG | LG-LB650, LG-HB650 | SRF |  | Controller, Ion Pump | SRF Warm units |  | 20 | Final | Off the Shelf | 15% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 2 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.29098 | 100 | 0.29098 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-155 | 121.3 | 121.3.06 | Vacuum | LT | LT-LB650 | SRF |  | Gauges, Ion | SRF Warm units |  | 20 | Final | Off the Shelf | 15% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 2 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-156 | 121.3 | 121.3.06 | Vacuum | LT | LT-HB650 | SRF |  | Gauges, Pirani | SRF Warm units |  | 20 | Final | Off the Shelf | 15% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 2 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-157 | 121.3 | 121.3.06 | Vacuum | LT | LT-HB650 | SRF |  | Controller, Ion/Pirani Gauge | SRF Warm units |  | 40 | Final | Off the Shelf | 15% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 4 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 2.4 | 100 | 2.4 | [12 empty] | Flexible <1cm (e.g. RG58) | 40 | Yes |  |  |  |  | C_Vacuum
DN-158 | 121.3 | 121.3.06 | Vacuum | LG | LG-HB650 | SRF |  | Racks | SRF Warm units |  | 2 | Final | Off the Shelf | 15% | Floor | 24 | 32 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 1 | 0.5 | [7 empty] | 0 | 0 | 100 | 0 | [7 empty] | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes |  | 4 | No |  |  | Ethernet | Additional 120V 10A circuit for network switch | C_Vacuum
DN-159 | 121.3 | 121.3.06 | Vacuum | LT | LT-LB650, LT-HB650 | SRF |  | Gate Valves | SRF Warm units |  | 30 | Final | Off the Shelf | 15% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 1.08 | 100 | 1.08 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-160 | 121.3 | 121.3.06 | Vacuum | LT | LT-LB650, LT-HB650 | Insulating Vac |  | Pump, Turbo | Insulating Vac |  | 24 | Final | Off the Shelf | 15% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 12 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 11.52 | 100 | 11.52 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 72 | Yes |  |  |  |  | C_Vacuum
DN-161 | 121.3 | 121.3.06 | Vacuum | LT | LT-LB650, LT-HB650 | Insulating Vac |  | Pump, Roughing | Insulating Vac |  | 24 | Final | Off the Shelf | 15% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 12 | 0.5 |  |  |  |  | 208 V - 1 Phase - 2 Wire | 208 | 5 | 1040 | 24.96 | 100 | 24.96 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | Yes |  |  |  |  | C_Vacuum
DN-162 | 121.3 | 121.3.06 | Vacuum | LT | LT-LB650, LT-HB650 | Insulating Vac |  | Gauges, Ion | Insulating Vac |  | 24 | Final | Off the Shelf | 15% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 2.4 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | No |  |  |  | powered through controller | C_Vacuum
DN-163 | 121.3 | 121.3.06 | Vacuum | LG | LG-LB650, LG-HB650 | Insulating Vac |  | Racks | Insulating Vac |  | 3 | Final | Off the Shelf | 15% | Floor | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 1.5 | 0.5 | [7 empty] | 0 | 0 | 100 | 0 | [7 empty] | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes |  | 6 | No |  |  | Ethernet | Additional 120V 10A circuit for network switch | C_Vacuum
DN-164 | 121.3 | 121.3.06 | Vacuum | LT | LT-HWR | HWR |  | Gate Valves | Fast Acting |  | 1 | Conceptual | Prototype-Testing | 30% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.036 | 100 | 0.036 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-165 | 121.3 | 121.3.06 | Vacuum | LT | LT-HB650 | HB650 |  | Gate Valves | Fast Acting |  | 1 | Conceptual | Prototype-Testing | 30% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.036 | 100 | 0.036 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-166 | 121.3 | 121.3.06 | Vacuum | LG | LG-HWR | HWR |  | Power Supply | HWR-SSR |  | 1 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 24 | 3.2 | 133.0215 | 0.13302 | 100 | 0.13302 | [12 empty] | Semi-rigid >1cm (e.g. 0.5" Heliax) |  | No |  |  |  | Rack Power supply (I may be doubling the load from the rack equipment) | C_Vacuum
DN-167 | 121.3 | 121.3.06 | Vacuum | LG | LG-LB650, LG-HB650 | SRF |  | Power Supply | SRF Warm units |  | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 24 | 7 | 290.9845 | 0.58197 | 100 | 0.58197 | [12 empty] | Semi-rigid >1cm (e.g. 0.5" Heliax) |  | No |  |  |  | Rack Power supply (I may be doubling the load from the rack equipment) | C_Vacuum
DN-168 | 121.3 | 121.3.06 | Vacuum | LG | LG-LB650, LG-HB650 | Insulating Vac |  | Controller, Ion/Pirani Gauge | Insulating Vac |  | 24 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 2.4 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 1.44 | 100 | 1.44 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-169 | 121.3 | 121.3.06 | Vacuum | LG | LG-LB650, LG-HB650 | Insulating Vac |  | Controller, Turbo Pump | Insulating Vac |  | 24 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [6 empty] | 120 | 0.5 | 103.923 | 2.4942 | 100 | 2.4942 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-170 | 121.3 | 121.3.06 | Vacuum | LG | LG-LB650, LG-HB650 | Insulating Vac |  | Power Supply | Insulating Vac |  | 3 | Final | Off the Shelf | 5% | Suspended | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 24 | 8.4 | 349.1814 | 1.0475 | 100 | 1.0475 | [12 empty] | Semi-rigid >1cm (e.g. 0.5" Heliax) |  | No |  |  |  | Rack Power supply (I may be doubling the load from the rack equipment) | C_Vacuum
DN-170.1 | 121.3 | 121.3.06 | Vacuum | LT | LT-LB650, LT-HB650 | Insulating Vac |  | Valves | Anti Suckback valves |  | 24 | Final | Off the Shelf | 5% | Beamline/Tunnel | [15 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [13 empty] | 24 | No |  |  |  |  | C_Vacuum
DN-171 | 121.3 | 121.3.06 | Vacuum | HBB | HBB-Upper High Bay | WFE |  | Racks | Rack Contains all Ion Pump Controllers, Turbo Pump Controlers, Gauge readbacks |  | 2 | Final | Off the Shelf | 5% | Floor | 24 | 32 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 1 | 0.5 | [7 empty] | 0 | 0 | 100 | 0 | [7 empty] | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes |  | 4 | No |  |  | Ethernet | Additional 120V 10A circuit for network switch | C_Vacuum
DN-172 | 121.3 | 121.3.06 | Vacuum | HBB | HBB-Upper High Bay | WFE |  | Power Supply |  |  | 1 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 24 | 2.45 | 101.8446 | 0.10184 | 100 | 0.10184 | [12 empty] | Semi-rigid >1cm (e.g. 0.5" Heliax) |  | No |  |  |  | Rack Power supply (I may be doubling the load from the rack equipment) | C_Vacuum
DN-173 | 121.3 | 121.3.06 | Vacuum | HBB | HBB-Lower High Bay | WFE |  | Pump, Ion |  |  | 9 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.9 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 9 | No |  |  |  | powered through controller | C_Vacuum
DN-174 | 121.3 | 121.3.06 | Vacuum | HBB | HBB-Lower High Bay | WFE |  | NEG |  |  | 2 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 2 | No |  |  |  | powered through controller | C_Vacuum
DN-174.1 | 121.3 | 121.3.06 | Vacuum | HBB | HBB-Upper High Bay | WFE |  | NEG Controller |  |  | 2 | Final | Off the Shelf | 5% | Rack Mounted | [15 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-175 | 121.3 | 121.3.06 | Vacuum | HBB | HBB-Lower High Bay | WFE |  | Pump, Turbo |  |  | 11 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 5.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 5.28 | 100 | 5.28 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 33 | Yes |  |  |  |  | C_Vacuum
DN-176 | 121.3 | 121.3.06 | Vacuum | HBB | HBB-Upper High Bay | WFE |  | Controller, Ion Pump |  |  | 9 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.9 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.13094 | 100 | 0.13094 | [12 empty] | Flexible <1cm (e.g. RG58) | 9 | No |  |  |  |  | C_Vacuum
DN-177 | 121.3 | 121.3.06 | Vacuum | HBB | HBB-Upper High Bay | WFE |  | Controller, Turbo Pump |  |  | 11 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 1 | 120 | 1.32 | 100 | 1.32 | [12 empty] | Flexible <1cm (e.g. RG58) | 11 | Yes |  |  |  |  | C_Vacuum
DN-178 | 121.3 | 121.3.06 | Vacuum | HBB | HBB-Lower High Bay | WFE |  | Gauges, Ion |  |  | 17 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 1.7 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 17 | No |  |  |  | powered through controller | C_Vacuum
DN-179 | 121.3 | 121.3.06 | Vacuum | HBB | HBB-Lower High Bay | WFE |  | Controller, Ion/Pirani Gauge |  |  | 17 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 1.7 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 1.02 | 100 | 1.02 | [12 empty] | Flexible <1cm (e.g. RG58) | 17 | Yes |  |  |  |  | C_Vacuum
DN-180 | 121.3 | 121.3.06 | Vacuum | BAL | BAL-Beam Asborber Space | BTL/BAL |  | Pump, Ion |  |  | 4 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 4 | No |  |  |  | powered through controller | C_Vacuum
DN-181 | 121.3 | 121.3.06 | Vacuum | BAL | BAL-Beam Asborber Space | BTL/BAL |  | Controller, Ion Pump |  |  | 4 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.058197 | 100 | 0.058197 | [12 empty] | Flexible <1cm (e.g. RG58) | 4 | No |  |  |  |  | C_Vacuum
DN-182 | 121.3 | 121.3.06 | Vacuum | BAL | BAL-Beam Asborber Space | BTL/BAL |  | Pump, Turbo |  |  | 2 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 1 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 0.96 | 100 | 0.96 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 6 | Yes |  |  |  |  | C_Vacuum
DN-183 | 121.3 | 121.3.06 | Vacuum | BAL | BAL-Beam Asborber Space | BTL/BAL |  | Controller, Turbo Pump |  |  | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 1 | 120 | 0.24 | 100 | 0.24 | [12 empty] | Flexible <1cm (e.g. RG58) | 2 | Yes |  |  |  |  | C_Vacuum
DN-184 | 121.3 | 121.3.06 | Vacuum | BAL | BAL-Beam Asborber Space | BTL/BAL |  | Gauges, Ion |  |  | 4 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 4 | No |  |  |  | powered through controller | C_Vacuum
DN-185 | 121.3 | 121.3.06 | Vacuum | BAL | BAL-Beam Asborber Space | BTL/BAL |  | Gauges, Pirani |  |  | 2 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 2 | No |  |  |  | powered through controller | C_Vacuum
DN-186 | 121.3 | 121.3.06 | Vacuum | BAL | BAL-Beam Asborber Space | BTL/BAL |  | Controller, Ion/Pirani Gauge |  |  | 6 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.6 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.36 | 100 | 0.36 | [12 empty] | Flexible <1cm (e.g. RG58) | 6 | Yes |  |  |  |  | C_Vacuum
DN-187 | 121.3 | 121.3.06 | Vacuum | BAL | BAL-Beam Asborber Space | BTL/BAL |  | Racks |  |  | 1 | Final | Off the Shelf | 5% | Floor | 24 | 32 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0.5 | 0.5 | [7 empty] | 0 | 0 | 100 | 0 | [7 empty] | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes |  | 2 | No |  |  | Ethernet | Additional 120V 10A circuit for network switch | C_Vacuum
DN-188 | 121.3 | 121.3.06 | Vacuum | BAL | BAL-Beam Asborber Space | BTL/BAL |  | Power Supply |  |  | 1 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 24 | 1.4 | 58.1969 | 0.058197 | 100 | 0.058197 | [12 empty] | Semi-rigid >1cm (e.g. 0.5" Heliax) |  | No |  |  |  | Rack Power supply (I may be doubling the load from the rack equipment) | C_Vacuum
DN-189 | 121.3 | 121.3.06 | Vacuum | LG | LG-BTL Power Supply | BTL/BAL |  | Racks |  |  | 2 | Final | Off the Shelf | 5% | Floor | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 1 | 0.5 | [7 empty] | 0 | 0 | 100 | 0 | [7 empty] | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes |  | 4 | No |  |  | Ethernet | Additional 120V 10A circuit for network switch | C_Vacuum
DN-190 | 121.3 | 121.3.06 | Vacuum | BTL | BTL-Beamline Tunnel | BTL/BAL |  | Pump, Ion |  |  | 53 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 5.3 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 53 | No |  |  |  | powered through controller | C_Vacuum
DN-191 | 121.3 | 121.3.06 | Vacuum | LG | LG-BTL Power Supply | BTL/BAL |  | Controller, Ion Pump |  |  | 53 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 5.3 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.77111 | 100 | 0.77111 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-192 | 121.3 | 121.3.06 | Vacuum | LG | LG-BTL Power Supply | BTL/BAL |  | Power Supply |  |  | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 24 | 18 | 748.2459 | 1.4965 | 100 | 1.4965 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | No |  |  |  | Rack Power supply (I may be doubling the load from the rack equipment) | C_Vacuum
DN-193 | 121.3 | 121.3.06 | Vacuum | BTL | BTL-Beamline Tunnel | BTL/BAL |  | Gauges, Ion |  |  | 8 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.8 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 8 | No |  |  |  |  | C_Vacuum
DN-194 | 121.3 | 121.3.06 | Vacuum | BTL | BTL-Beamline Tunnel | BTL/BAL |  | Gauges, Pirani |  |  | 8 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.8 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 8 | No |  |  |  |  | C_Vacuum
DN-195 | 121.3 | 121.3.06 | Vacuum | LG | LG-BTL Power Supply | BTL/BAL |  | Controller, Ion/Pirani Gauge |  |  | 4 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.24 | 100 | 0.24 | [12 empty] | Flexible <1cm (e.g. RG58) | 4 | Yes |  |  |  |  | C_Vacuum
JH-001 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Skids | Vane Cooling Skid |  | 1 | Final | Off the Shelf | 5% | Floor | 70 | 24 | 60 | 600 |  | Yes | Sealed concrete | 65 | 78 | 60 max |  |  |  | Air, Environment | 1.12 | 1.12 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 7 | 5819.6907 | 5.8197 | 100 | 5.8197 |  |  |  |  | Yes | [9 empty] | Yes |  |  |  |  | C_WFE
JH-001-A | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Skids | Vane Cooling Skid |  | 0 | Final | Off the Shelf | 5% | [14 empty] | Chilled LCW | 38 | 38 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 0.6 | 100 | 0.6 | [14 empty] | Yes |  |  |  | Added 120V circuit for controls | C_WFE
JH-002 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Skids | Wall Cooling Skid |  | 1 | Final | Off the Shelf | 5% | Floor | 88 | 24 | 70 | 1200 |  | Yes | Sealed concrete | 65 | 78 | 60 max |  |  |  | Air, Environment | 2.24 | 2.24 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 13.4 | 11140.5508 | 11.1406 | 100 | 11.1406 |  |  |  |  | Yes | [9 empty] | Yes |  |  |  |  | C_WFE
JH-002-A | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Skids | Wall Cooling Skid |  | 0 | Final | Off the Shelf | 5% | [14 empty] | Chilled LCW | 65 | 65 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 0.6 | 100 | 0.6 | [14 empty] | Yes |  |  |  | Heat load assumes 30% contingency. Added 120V circuit for controls | C_WFE
JH-003 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Skids | Intermediate Cooling Skid |  | 0 | Preliminary | Prototype-Testing | 25% | Floor | 84 | 36 | 78 | 1800 |  | Yes | Sealed concrete | 65 | 78 | 60 max |  |  |  | Air, Environment | 3 | 3 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 0.6 | 100 | 0.6 | [14 empty] | Yes |  |  |  | Added 120V circuit for controls | C_WFE
JH-003-A | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Skids | Intermediate Cooling Skid |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 175 | 29 | 66 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Chilled LCW | 0 | 0 |  | 86 | 90 | 1 | 10 | 480 V - 3 Phase - 3 Wire | 480 | 60 | 49883.0633 | 49.8831 | 100 | 49.8831 |  |  | 60 |  | Yes | [9 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_WFE
JH-004-A | 121.4 | 121.4.03 | BldgI | PUB | PUB | LCW |  | Pump | Circulating Pump |  | 3 | Preliminary | Prototype-Testing | 25% | Floor | 98 | 26 | 40 |  |  | Yes | Sealed concrete | 65 | 115 | 75 |  |  |  | Air, Environment | 37 | 111 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 224 | 186230.1028 | 558.6903 | 100 | 558.6903 |  |  |  |  | Yes | Yes | [8 empty] | Yes |  |  |  | 3 pumps | C_BldgI
JH-004-B | 121.4 | 121.4.03 | BldgI | PUB | PUB | LCW |  | Pump | Standby Circulating Pump | 3 | 1 | Preliminary | Prototype-Testing | 25% | Floor | 98 | 26 | 40 |  |  | Yes | Sealed concrete | 65 | 115 | 75 | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 |  |  |  |  | Yes | Yes | [8 empty] | No |  |  |  | 1 standby spare. Allocated only space for spare
JH-005 | 121.4 | 121.4.03 | BldgI | PUB | PUB | LCW |  | Tank | Expansion Tank |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 72 | 72 | 120 | 15000 |  | No | Sealed concrete | 65 | 115 | 75 | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_BldgI
JH-006 | 121.4 | 121.4.03 | BldgI | PUB | PUB | LCW |  | Heat Exchanger | LCW Heat Exchanger |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 150 | 48 | 120 | 22000 |  | No | Sealed concrete | 65 | 115 | 75 |  |  |  | ICW |  | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | Based on 10 deg F delta T, 88 F supply temp, 11 MW Heat Load. 40% efficiency on Power Amplifiers | C_BldgI
JH-007 | 121.4 | 121.4.03 | BldgI | PUB | PUB | Dissolved Oxygen |  | Skids |  |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 42 | 24 | 72 | 1200 |  | Yes | Sealed concrete | 65 | 115 | 75 |  |  |  | ICW | 0.1 | 0.1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 6.2 | 744 | 0.744 | 100 | 0.744 | [14 empty] | Yes |  |  |  | 1/3 hp, 20% heat load, minimal | C_BldgI
JH-008 | 121.4 | 121.4.03 | BldgI | PUB | PUB | Resistivity Control |  | Bottles |  |  | 3 | Preliminary | Prototype-Testing | 25% | Floor | 18 | 18 | 60 | 300 |  | No | Sealed concrete | 65 | 115 | 75 | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_BldgI
JH-009-A | 121.4 | 121.4.03 | BldgI | PUB | PUB | Compressed Air |  | Air Compressor |  |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 64 | 30 | 60 |  |  | Yes | Sealed concrete | 65 | 115 | 75 |  |  |  | Air, Environment | 12 | 12 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 66.6 | 55370.2002 | 55.3702 | 100 | 55.3702 |  |  |  |  | Yes | Yes | [8 empty] | Yes |  |  |  | out of 40 hp, 80% goes to air (run 1 + 1 standby spare) | C_BldgI
JH-009-B | 121.4 | 121.4.03 | BldgI | PUB | PUB | Compressed Air |  | Air Compressor | Standby | 1 | 1 | Preliminary | Off the Shelf | 5% | Floor | 64 | 30 | 60 |  |  | Yes | Sealed concrete | 65 | 115 | 75 | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 |  |  |  |  | Yes | Yes | [8 empty] | No |  |  |  | 1 standby spare. Allocated only space for spare
JH-010-A | 121.4 | 121.4.03 | BldgI | PUB | PUB | Compressed Air |  | Dryer | Desiccant Dryer |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 27 | 20 | 37 |  |  | Yes | Sealed concrete | 65 | 115 | 75 |  |  |  | Air, Environment | 0.1 | 0.1 | [5 empty] | 240 V - 1 Phase - 2 Wire | 230 | 6.8 | 1564 | 1.564 | 100 | 1.564 | [14 empty] | Yes |  |  |  |  | C_BldgI
JH-010-B | 121.4 | 121.4.03 | BldgI | PUB | PUB | Compressed Air |  | Dryer | Standby Desiccant Dryer | 1 | 1 | Preliminary | Off the Shelf | 5% | Floor | 27 | 20 | 37 |  |  | Yes | Sealed concrete | 65 | 115 | 75 | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | 1 standby spare. Allocated only space for spare
JH-011 | 121.4 | 121.4.03 | BldgI | PUB | PUB | Compressed Air |  | Tank |  |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 36 | 36 | 80 |  |  | No | Sealed concrete | 65 | 115 | 75 | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_BldgI
JH-012 | 121.4 | 121.4.03 | BldgI | PUB | PUB | Compressed Air |  | Water/Oil Separator |  |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 32 | 16 | 32 |  |  | No | Sealed concrete | 65 | 115 | 75 | [5 empty] | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 0.6 | 100 | 0.6 | [14 empty] | Yes |  |  |  |  | C_BldgI
JH-013 | 121.4 | 121.4.02 | WFE | HBB | HBB-Upper High Bay | Ion Source |  | Skids | Cooling Skid |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 70 | 24 | 60 | 300 |  | Yes | Sealed concrete | 65 | 78 | 60 max |  | 0 | 0 | Air, Environment | 0.4 | 0.4 |  | 72 | 80 | +/- 1 | 10 | 480 V - 3 Phase - 3 Wire | 480 | 3 | 2494.1532 | 2.4942 | 80 | 1.9953 | NA | NA | 20 | N/A | Yes |  | Yes | [7 empty] | Yes | No | Yes | ACNET |  | C_WFE
JH-016 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | Ion Source |  | Cabinets | LV cabinet |  | 2 | Preliminary | Prototype-Testing | 25% | Floor | 31 | 31 | 87 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.1 | 0.2 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 3.6 | 100 | 3.6 |  |  | 15 |  |  | Yes | Yes | [7 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_WFE
JH-017 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | Ion Source |  | Cabinets | HV cabinet |  | 2 | Preliminary | Prototype-Testing | 25% | Floor | 40 | 40 | 87 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.1 | 0.2 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 40 | 33255.3755 | 66.5108 | 100 | 66.5108 |  |  | 40 |  |  | Yes | Yes | [7 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_WFE
JH-018 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | Ion Source |  | Ion Source | Ion source enclosure |  | 2 | Conceptual | Prototype-Testing | 25% | Floor | 28 | 29 | 103 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment |  | 0 | [8 empty] | 0 | 0 | 100 | 0 | [5 empty] | Yes | [8 empty] | No |  |  |  |  | C_WFE
JH-018-A | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | Ion Source |  | Ion Source | Ion source (all components) |  | 0 | Final | Prototype-Testing | 25% | [8 empty] | 65 | 78 | 60 max |  |  |  | Chilled LCW | 12 | 24 |  | 72 | 80 | +/- 1 |  |  |  |  | 0 | 0 | 100 | 0 | [6 empty] | Yes | [7 empty] | No |  |  |  |  | C_WFE
JH-019 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | Ion Source |  | Bottle Enclosure | Hydrogen bottle enclosure |  | 1 | Conceptual | Prototype-Testing | 25% | Floor | 21 | 17 | 30 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment |  | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-020 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | Ion Source |  | Panels | Electrical panel for Bias PS/CDC |  | 2 | Preliminary | Prototype-Testing | 25% | Suspended | 24 | 24 | 10 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.05 | 0.1 | [5 empty] | 208 V - 1 Phase - 2 Wire | 208 | 15 | 3120 | 6.24 | 100 | 6.24 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_WFE
JH-021 | 121.4 | 121.4.02 | WFE | HBB | HBB-Upper High Bay | LEBT |  | Racks | Rack with solenoid power supplies |  | 2 | Final | Off the Shelf | 5% | Floor | 24 | 32 | 63 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 1 | 0.5 |  |  |  |  | 480 V - 3 Phase - 3 Wire | 480 | 48 | 39906.4506 | 79.8129 | 100 | 79.8129 |  |  | 60 | [11 empty] | Yes | No |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the controllers | C_WFE
JH-022 | 121.4 | 121.4.02 | WFE | HBB | HBB-Upper High Bay | LEBT |  | Racks | Rack with solenoid power supplies controllers |  | 2 | Final | Off the Shelf | 5% | Floor | 24 | 32 | 63 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 1 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 3.6 | 100 | 3.6 |  |  | 15 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the power supplies | C_WFE
JH-023 | 121.4 | 121.4.02 | WFE | HBB | HBB-Upper High Bay | LEBT |  | Racks | Rack with Dipole power supply and controller |  | 1 | Final | Off the Shelf | 5% | Rack Mounted | 24 | 30 | 14 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Spatial requirements for "Height" is the height occupied within the rack; Power requirement is from breaker rating at PIP2IT | C_WFE
JH-024 | 121.4 | 121.4.02 | WFE | HBB | HBB-Upper High Bay | LEBT |  | Racks | Rack with correctors power supplies |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 24 | 30 | 84 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 480 V - 3 Phase - 3 Wire | 480 | 48 | 39906.4506 | 39.9065 | 100 | 39.9065 |  |  | 60 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the controllers | C_WFE
JH-025 | 121.4 | 121.4.02 | WFE | HBB | HBB-Upper High Bay | LEBT |  | Racks | Rack with correctors power supplies controllers |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 24 | 30 | 84 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the power supplies | C_WFE
JH-026 | 121.4 | 121.4.02 | WFE | HBB | HBB-Upper High Bay | WFE |  | Racks | Rack with stepper motor bulk power supply |  | 2 | Preliminary | Off the Shelf | 5% | Floor | 24 | 30 | 75 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 1 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 3.6 | 100 | 3.6 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the controllers | C_WFE
JH-027 | 121.4 | 121.4.02 | WFE | HBB | HBB-Upper High Bay | WFE |  | Racks | Rack with stepper motor controllers |  | 2 | Preliminary | Off the Shelf | 5% | Floor | 24 | 30 | 75 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 1 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 3.6 | 100 | 3.6 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the power supplies | C_WFE
JH-028 | 121.4 | 121.4.02 | WFE | HBB | HBB-Upper High Bay | LEBT |  | Power Supplies | LEBT chopper power supply |  | 1 | Preliminary | Off the Shelf | 5% | Rack Mounted | 19 | 30 | 3.5 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.05 | 0.05 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Within WFE footprint | C_WFE
JH-029 | 121.4 | 121.4.02 | WFE | HBB | HBB-Upper High Bay | LEBT |  | Power Supplies | LEBT chopper DC offset power supply |  | 1 | Preliminary | Off the Shelf | 5% | Rack Mounted | 19 | 30 | 3.5 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.05 | 0.05 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Within WFE footprint | C_WFE
JH-030 | 121.4 | 121.4.02 | WFE | HBB | HBB-Upper High Bay | WFE |  | Cabinets | Rittal cabinet for LCW (including RFQ skid controller) |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 103 | 16 | 83 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_WFE
JH-032 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Couplers | Power coupler body |  | 2 | Final | Off the Shelf | 5% | RFQ Mounted | [7 empty] | 65 | 78 | 60 max |  |  |  | LCW | 0.3 | 0.6 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-033 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Couplers | Power coupler antenna |  | 2 | Final | Off the Shelf | 5% | RFQ Mounted | [7 empty] | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.12 | 0.24 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-034 | 121.4 | 121.4.02 | WFE | HBB | HBB-Upper High Bay | RFQ |  | Power Supplies | RFQ couplers bias power supply |  | 1 | Final | Off the Shelf | 5% | Rack Mounted | 24 | 30 | 5 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.05 | 0.05 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Single unit in standard rack; Power requirement is from breaker rating at PIP2IT | C_WFE
JH-035 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Power Amplifiers |  |  | 2 | Final | Off the Shelf | 5% | Floor | 94 | 40 | 90 |  |  |  |  | 65 | 78 | 60 max |  |  |  | LCW | 150 | 300 |  | 86 |  | 1 | 10 | 480 V - 3 Phase - 3 Wire | 480 | 180 | 149649.1898 | 299.2984 | 100 | 299.2984 |  |  |  |  | Yes | [9 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_WFE
JH-036 | 121.3 | 121.3.05 | Magnets | HBB | HBB-Upper High Bay | MEBT |  | Racks | Rack with quadrupole power supplies and controllers |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 24 | 30 | 75 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_Magnets
JH-037 | 121.3 | 121.3.05 | Magnets | HBB | HBB-Upper High Bay | MEBT |  | Racks | Rack with dipole correctors power supplies and controllers |  | 1 | Pre-conceptual | Prototype-Testing | 25% | Floor | 24 | 30 | 75 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_Magnets
JH-038 | 121.3 | 121.3.05 | Magnets | HBB | HBB-Upper High Bay | MEBT |  | Racks | Rack with dipole correctors bulk power supply |  | 1 | Pre-conceptual | Prototype-Testing | 25% | Floor | 24 | 30 | 75 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the correctors power supplies and controllers | C_Magnets
JH-039 | 121.3 | 121.3.05 | Magnets | HBB | HBB-Upper High Bay | MEBT |  | Racks | Rack with dipole correctors bulk power supply |  | 1 | Pre-conceptual | Prototype-Testing | 25% | Floor | 24 | 30 | 75 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the correctors power supplies and controllers | C_Magnets
JH-040 | 121.4 | 121.4.02 | WFE | HBB | HBB-Upper High Bay | MEBT |  | Racks | Rack with bunching cavities amplifiers and controllers |  | 2 | Preliminary | Off the Shelf | 5% | Floor | 24 | 30 | 99 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 1 | 0.5 |  |  |  |  | 208 V - 3 Phase - 3 Wire | 208 | 30 | 10807.997 | 21.616 | 100 | 21.616 |  |  | 30 | [11 empty] | Yes |  |  |  | Standard rack; Power requirement is from breaker rating at PIP2IT | C_WFE
JH-041 | 121.4 | 121.4.02 | WFE | HBB | HBB-Upper High Bay | WFE |  | Racks | Rack with electrodes biasing power supplies and current readouts electronics |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 24 | 30 | 99 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | All units occupy 1/2 rack | C_WFE
JH-042 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | MEBT |  | Bunching Cavities |  |  | 4 | Final | Prototype-Testing | 25% | Beamline/Tunnel | [7 empty] | 65 | 78 | 60 max |  |  |  | LCW | 1.5 | 6 |  | 86 | 88 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-043 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | MEBT |  | Scrapers Vacuum Chamber |  |  | 4 | Final | Prototype-Testing | 25% | Beamline/Tunnel | [7 empty] | 65 | 78 | 60 max |  |  |  | LCW | 0.3 | 1.2 |  | 86 | 88 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-044 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | MEBT |  | Absorber Assembly |  |  | 1 | Preliminary | Prototype-Testing | 25% | Beamline/Tunnel | [7 empty] | 65 | 78 | 60 max |  |  |  | LCW | 20 | 20 |  | 86 | 88 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | 10 gpm | C_WFE
JH-045 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | MEBT |  | Kickers |  |  | 2 | Final | Prototype-Testing | 25% | Beamline/Tunnel | [7 empty] | 65 | 78 | 60 max |  |  |  | LCW | 0.5 | 1 |  | 86 | 88 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-046 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | LEBT |  | Solenoids |  |  | 4 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 65 | 78 | 60 max |  |  |  | LCW | 7.5 | 30 |  | 86 | 88 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-047 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | LEBT |  | Magnets | Bending dipole |  | 1 | Final | Prototype-Testing | 25% | Beamline/Tunnel | [7 empty] | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.05 | 0.05 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-049 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | LEBT |  | Chopper |  |  | 1 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 65 | 78 | 60 max |  |  |  | LCW | 0.3 | 0.3 |  | 86 | 88 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-052 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | Ion Source |  | Allison Scanner |  |  | 4 | Final | Prototype-Testing | 25% | Beamline/Tunnel | 24 | 30 | 98 |  |  |  |  | 65 | 78 | 60 max |  |  |  | LCW | 0.6 | 2.4 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-053 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Circulators |  |  | 2 | Preliminary | Prototype-Testing | 25% | Suspended | 11 | 30 | 34 |  |  |  |  | 65 | 78 | 60 max |  |  |  | LCW | 0 | 0 |  | 86 |  | 1 | 10 |  |  |  | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-054 | 121.4 | 121.4.02 | WFE | HBB | HBB-Lower High Bay | MEBT |  | Power Supplies | Chopper HV Power supplies |  | 4 | Preliminary | Prototype-Testing | 25% | Suspended | 24 | 30 | 5 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.1 | 0.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 7.2 | 100 | 7.2 |  |  | 20 | [11 empty] | Yes |  |  |  |  | C_WFE
JH-055 | 121.4 | 121.4.03 | BldgI | LG | LG-General |  | AC Distribution |  | HLA for AC Distribution Cables |  |  | Preliminary | Expert Opinion | 50% | [14 empty] | Air, Environment |  | 0 | 120 | [7 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_BldgI
JO-001 | 121.2 | 121.2.02 | HWR | LT | LT-HWR | HWR Cryomodule |  | Cryomodule |  |  | 1 | Final | Off the Shelf | 5% | Floor | 244.1 | 78.74 | 78.74 | 18580 |  | TBD | Sealed concrete | [7 empty] | NA | 0 |  | 70 | 75 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No | Yes | No | NA | CM Space requirement is CM only - no "keep clear" or access volume added. Air cooling is for coupler, 800SCFH total. | C_HWR
JO-002 | 121.2 | 121.2.02 | HWR | LT | LT-HWR | Vacuum, Insulating |  | Pumps and Controllers | Roughing and Turbo Pumps |  | 1 | Final | Off the Shelf | 5% | Floor | [5 empty] | TBD | Sealed concrete | [5 empty] | 283 | Chilled Water | 1.5 | 1.5 |  | 60 | 68 |  |  | 120 V - 1 Phase - 2 Wire | 120 | 12.1 | 1452 | 1.452 | 100 | 1.452 |  |  | 20 |  | No | No | No | [7 empty] | Yes | No | No | Other (specify) | Ins vac pump occupies space underneath CM, no additional floor space needed. Comms via RS232/484/485. Chilled water flow of 9-20 GPH at 50-68F. 2-20A breakers | C_HWR
JO-003 | 121.2 | 121.2.02 | HWR | LT | LT-HWR | Vacuum, Cavity |  | Pumps and Controllers | Roughing and Turbo Pumps |  | 1 | Final | Off the Shelf | 5% | Floor | [5 empty] | TBD | Sealed concrete | [5 empty] | 71 | Chilled Water | 0.5 | 0.5 |  | 60 | 68 |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3 | 360 | 0.36 | 100 | 0.36 |  |  | 20 |  | No | No | No | [7 empty] | Yes | No | No | Other (specify) | Cav vac pump occupies space underneath CM, no additional floor space needed. Comms via RS232/484/485. Chilled water flow of 5 GPH at 60F. 2-20A breakers | C_HWR
JO-004 | 121.2 | 121.2.02 | HWR | LT | LT-HWR | HWR Cryomodule |  | Couplers | 8 cavities x 1 CM |  | 8 | Final | Prototype-Testing | 25% | [14 empty] | Air, Environment | 0.025 | 0.2 | 0.2 | 70 | 75 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | Air cooling is for coupler, 800SCFH (13.3 SCFM) total, < 40deg F dew point, compressed air | C_HWR
JO-005 | 121.2 | 121.2.04 | LBHB | LT | LT-LB650 | LB650 |  | Cryomodule |  |  | 11 | Conceptual | Expert Opinion | 50% | Floor | 255 | 82 | 88 | 21000 |  | TBD | Sealed concrete | [8 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No | Yes | No | NA |  | C_LBHB
JO-006 | 121.2 | 121.2.04 | LBHB | LT | LT-HB650 | HB650 |  | Cryomodule |  |  | 6 | Preliminary | Expert Opinion | 50% | Floor | 391 | 82 | 88 | 27700 |  | TBD | Sealed concrete | [8 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 |  |  |  |  | No | No | No | [7 empty] | No | Yes | No | NA |  | C_LBHB
JO-007 | 121.2 | 121.2.04 | LBHB | LT | LT-LB650 | LB650 |  | Couplers | 3 cavities x 11 CMs |  | 33 | Conceptual | Expert Opinion | 50% | [14 empty] | Air, Compressed | 0.30667 | 10.12 |  | 70 | 75 | [5 empty] | 0 | 0 | 100 | 0 |  |  |  |  | No | No | No | [7 empty] | No | No | No | NA | Air flow = 16.5 SCFM | C_LBHB
JO-008 | 121.2 | 121.2.04 | LBHB | LT | LT-HB650 | HB650 |  | Couplers | 6 cavities x 6 CMs |  | 36 | Preliminary | Prototype-Testing | 25% | [14 empty] | Air, Compressed | 0.45833 | 16.5 |  | 70 | 75 | [5 empty] | 0 | 0 | 100 | 0 |  |  |  |  | No | No | No | [7 empty] | No | No | No | NA | Air flow = 33 SCFM | C_LBHB
JO-009 | 121.2 | 121.2.03 | SSR | LT | LT-SSR1 | SSR1 |  | Cryomodule |  |  | 2 | Final | Off the Shelf | 5% | Floor | 212.6 | 86.6 | 112.2 | 26400 |  | TBD | Sealed concrete | [8 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No | Yes | No | NA |  | C_SSR
JO-010 | 121.2 | 121.2.03 | SSR | LT | LT-SSR2 | SSR2 |  | Cryomodule |  |  | 7 | Preliminary | Prototype-Testing | 25% | Floor | 255.9 | 86.6 | 112.2 | 26400 |  | TBD | Sealed concrete | [8 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 |  |  |  |  | No | No | No | [7 empty] | No | Yes | No | NA |  | C_SSR
JO-011 | 121.2 | 121.2.03 | SSR | LT | LT-SSR1 | SSR1 |  | Couplers | 8 cavities x 2 CMs |  | 16 | Final | Prototype-Testing | 25% | [14 empty] | Air, Compressed | 0.051 | 0.816 |  | 70 | 75 | [5 empty] | 0 | 0 | 100 | 0 |  |  |  |  | No | No | No | [7 empty] | No | No | No | NA | Air flow = 16 SCFM | C_SSR
JO-012 | 121.2 | 121.2.03 | SSR | LT | LT-SSR2 | SSR2 |  | Couplers | 5 cavities x 7 CMs |  | 35 | Preliminary | Prototype-Testing | 25% | [14 empty] | Air, Compressed | 0.18 | 6.3 |  | 70 | 75 | [5 empty] | 0 | 0 | 100 | 0 |  |  |  |  | No | No | No | [7 empty] | No | No | No | NA | Air flow = 15 SCFM | C_SSR
JO-013 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Cold Box Equipment |  |  | 1 | Final | Off the Shelf | 5% | Floor | 590.4 | 315 | 276 | 165347 | F(F) 25, F(L) 20 |  | Sealed concrete | [6 empty] | Chilled Water |  | 0 |  | 60 |  |  |  | 480 V - 3 Phase - 3 Wire | 480 | 70 | 58196.9071 | 58.1969 | 100 | 58.1969 |  |  |  |  | Yes | [9 empty] | Yes | No |  |  | 60 gpm for entire cold box station at 60 deg F or higher | C_CP
JO-014 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Cold Box Equipment |  |  | 1 | Final | Off the Shelf | 5% | [8 empty] | 78 | 68 | 55 | [5 empty] | 0 | [5 empty] | 240 V - 1 Phase - 2 Wire | 240 | 10 | 2400 | 2.4 | 100 | 2.4 |  |  |  |  | Yes | [9 empty] | Yes | No |  |  |  | C_CP
JO-015 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Cold Box Equipment |  |  | 1 | Final | Off the Shelf | 5% | [8 empty] | 78 | 68 | 55 | [5 empty] | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 110 | 13200 | 13.2 | 100 | 13.2 |  |  |  |  | Yes | [9 empty] | Yes | No |  |  |  | C_CP
JO-016 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Cold Box Equipment |  |  | 1 | Final | Off the Shelf | 5% | [8 empty] | 78 | 68 | 55 |  | 45,000 cfm in upper 10,000 cfm in lower portion |  | Air, Environment | 15 | 15 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No | No |  |  |  | C_CP
JO-017 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Cold Box Station |  | 4.5K Cold Box |  |  | 1 | Final | Off the Shelf | 5% | Floor | 74.4 | 63.6 | 188.4 | 6266 |  |  |  | 78 | 68 | 55 | [5 empty] | 0 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 3.6 | 2992.9838 | 2.993 | 100 | 2.993 |  |  |  |  | Yes | [9 empty] | Yes | No |  |  |  | C_CP
JO-018 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Cold Box Station |  | 4.5K Cold Box |  |  | 1 | Final | Off the Shelf | 5% | [8 empty] | 78 | 68 | 55 | [5 empty] | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 30 | 3600 | 3.6 | 100 | 3.6 |  |  |  |  | Yes | [9 empty] | Yes | No |  |  |  | C_CP
JO-019 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Racks | Cryo Control Cab |  | 4 | Final | Off the Shelf | 5% | Floor | 32.2 | 21 | 88.8 | 50 |  |  |  | 78 | 68 | 55 |  |  |  | Air, Environment | 0.5 | 2 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 30 | 3600 | 14.4 | 100 | 14.4 |  |  |  |  | Yes | [9 empty] | Yes | No |  |  |  | C_CP
JO-020 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Storage Tank | Lhe |  | 1 | Conceptual | Completely Unknown | 100% | Floor | [7 empty] | 78 | 68 | 55 | [5 empty] | 0 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 6 | 4988.3063 | 4.9883 | 100 | 4.9883 | [14 empty] | Yes | No |  |  |  | C_CP
JO-021 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Welding Receptacle |  |  | 1 | Final | Off the Shelf | 5% | Suspended | [7 empty] | 78 | 68 | 55 | [5 empty] | 0 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 60 | 49883.0633 | 49.8831 | 100 | 49.8831 |  |  |  |  | Yes | [9 empty] | Yes | No |  |  |  | C_CP
JO-022 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Generator | For UPS |  | 1 | Conceptual | Completely Unknown | 100% | Floor | [7 empty] | 78 | 68 | 55 | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | 25 |  |  |  | Yes | TBD | [8 empty] | No | No |  |  |  | C_CP
JO-023 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Compressors | Mycom |  | 1 | Final | Off the Shelf | 5% | Floor | 139.2 | 69.6 | 88.8 | 7000 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None |  |  |  | ICW | 83 | 83 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 600 | 498830.6326 | 498.8306 | 100 | 498.8306 | [14 empty] | Yes |  |  |  | ICW @ 200 gpm | C_CP
JO-024 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | SP |  | 1 | Final | Off the Shelf | 5% | Floor | 220.8 | 122.4 | 174 | 26455 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None |  |  |  | ICW | 917 | 917 | [5 empty] | Other (specify) | 4160 | 55.5 | 399895.8905 | 399.8959 | 100 | 399.8959 | [14 empty] | Yes |  |  |  | ICW @ 240 gpm | C_CP
JO-025 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | LP |  | 1 | Final | Off the Shelf | 5% | Floor | 220.8 | 122.4 | 174 | 26455 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | ICW @ 240 gpm | C_CP
JO-026 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | HP |  | 2 | Final | Off the Shelf | 5% | Floor | 220.8 | 122.4 | 174 | 26455 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None |  |  |  | ICW | 1400 | 2800 | [5 empty] | Other (specify) | 4160 | 100 | 720533.1359 | 1441.0663 | 100 | 1441.0663 | [14 empty] | Yes |  |  |  | ICW @ 480 gpm | C_CP
JO-027 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Panels | Gas Mgmt |  | 2 | Final | Off the Shelf | 5% | Floor | 196.8 | 39.6 | 86.4 | 3750 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_CP
JO-028 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | Oil Absorber |  | 1 | Final | Off the Shelf | 5% | Floor | 91.2 | 76.8 | 146.4 | 8160 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 37 | 30761.2223 | 30.7612 | 100 | 30.7612 | [14 empty] | Yes |  |  |  |  | C_CP
JO-029 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | Oil Coalscr |  | 1 | Final | Off the Shelf | 5% | Floor | 139.2 | 40.8 | 110.4 | 5511 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_CP
JO-030 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | Oil Dryer |  | 1 | Final | Off the Shelf | 5% | Floor | 74.4 | 78 | 100.8 | 1984 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_CP
JO-031 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | LP Oil Absrbr |  | 3 | Final | Off the Shelf | 5% | Floor | 393.6 | 141.6 | 178.8 | 39685 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 37 | 30761.2223 | 92.2837 | 100 | 92.2837 | [14 empty] | Yes |  |  |  |  | C_CP
JO-032 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Racks | SP/LP Control Cab |  | 1 | Final | Off the Shelf | 5% | Floor | 189.6 | 24 | 86.4 | 2200 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None |  |  |  | Air, Environment | 0.5 | 0.5 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 20 | 16627.6878 | 16.6277 | 100 | 16.6277 | [14 empty] | Yes |  |  |  |  | C_CP
JO-033 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Racks | HP Control Cab |  | 1 | Final | Off the Shelf | 5% | Floor | 157.2 | 24 | 86.4 | 2200 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None |  |  |  | Air, Environment | 0.5 | 0.5 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 20 | 16627.6878 | 16.6277 | 100 | 16.6277 | [14 empty] | Yes |  |  |  |  | C_CP
JO-034 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Racks | Inventory Ctrl Cab |  | 1 | Final | Off the Shelf | 5% | Floor | 139.2 | 40.8 | 110.4 | 1000 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None |  |  |  | Air, Environment | 0.5 | 0.5 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 20 | 16627.6878 | 16.6277 | 100 | 16.6277 | [14 empty] | Yes |  |  |  |  | C_CP
JO-035 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | Purifier Skid |  | 1 | Final | Off the Shelf | 5% | Floor | 36 | 36 | 117.6 | 2200 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_CP
JO-036-A | 121.2 | 121.2.05 | CP | PUB | PUB | Warm Compressor Section |  | Compressors | Air |  | 1 | Final | Off the Shelf | 5% | Floor | 81.6 | 40.8 | 67.2 | 500 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None |  |  |  | Air, Environment | 44 | 44 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 110 | 91452.2826 | 91.4523 | 100 | 91.4523 | [14 empty] | Yes |  |  |  |  | C_CP
JO-036-B | 121.2 | 121.2.05 | CP | PUB | PUB | Warm Compressor Section |  | Compressors | Standby Air Compressor |  | 1 | Final | Off the Shelf | 5% | Floor | 81.6 | 40.8 | 67.2 | 500 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | Allocated space only for 1 standby
JO-037 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Welding Receptacle | Weld Receptacle |  | 1 | Final | Off the Shelf | 5% | Suspended | [7 empty] | 68 | Amb + 10 | None | [5 empty] | 0 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 60 | 49883.0633 | 49.8831 | 100 | 49.8831 | [14 empty] | Yes |  |  |  |  | C_CP
JO-038 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Entire Area |  |  | 1 | Final | Off the Shelf | 5% | [8 empty] | 68 | Amb + 10 | None |  | 45,000 cfm in upper 10,000 cfm in lower portion |  | Air, Environment | 200 | 200 | [8 empty] | 0 | 0 | 100 | 0 | 25 | [13 empty] | No | No |  |  |  | C_CP
JO-039 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Network Room |  | Entire Area |  |  | 1 | Final | Off the Shelf | 5% | [8 empty] | 68 | 78 | 55 | Yes |  |  |  |  | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No | No |  |  |  | C_CP
JO-040 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Network Room |  | Racks | Main Network Room | 2 | 3 | Final | Off the Shelf | 5% | Floor | 24 | 48 | 96 | [10 empty] | Air, Environment | 0.5 | 1.5 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 30 | 3.2 | 166.2769 | 0.49883 | 100 | 0.49883 | [7 empty] | Other | Open | Left AND Right | Closed | Yes |  |  | No |  |  |  | 1-30A/208V ckt fed from UPS, 1 30A/208V ckt fed from bldg pwr, 1 20A/120V ckt fed from bldg pwr | C_CP
JO-041 | 121.2 | 121.2.05 | CP | CP | Cryoplant Building | Network Room |  | Racks | Cryo Specific Rack |  | 2 | Final | Off the Shelf | 5% | Floor | 24 | 48 | 96 | [10 empty] | Air, Environment | 0.5 | 1 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 30 | 3.2 | 166.2769 | 0.33255 | 100 | 0.33255 | [7 empty] | Other | Open | Left AND Right | Closed | Yes |  |  | No |  |  |  | 1-30A/208V ckt fed from UPS, 1 30A/208V ckt fed from bldg pwr, 1 20A/120V ckt fed from bldg pwr | C_CP
Note on AZ16: Racks should be listed as a separate row to ensure the location and quantity are captured correctly.
Note on T17: Jonathan W. Hunt x 15287N: Is this necessary? Should we just delete? Or add N/A for items not necessary?
Note on Z17: Enter an acceptable range with minimum and maximum humidity levels, if applicable (e.g. 30-60%, or 0-90% if no minimum humidity requirement)
Note on AJ17: This is a stability requirement of the water supply temperature, and may not be necessary in most cases. Format shall be +/- in degrees F.
Note on BE17: Choose the least flexible cable type
Note on BF20: Duane L. Newhart x6378,3721,6378 11580N: rack only have power and ethernet counted here. One of each per rack
Note on BF22: Duane L. Newhart x6378,3721,6378 11580N: cable type: Thermal couple; 6C16 LVDT/LimitSwitches: 18g multi
Note on BF26: Duane L. Newhart x6378,3721,6378 11580N: plus 1 per supply ethernet and 1 RG58
Note on BF27: Duane L. Newhart x6378,3721,6378 11580N: plus 1 ethernet per supply and 1 RG58
Note on BF28: Duane L. Newhart x6378,3721,6378 11580N: Also 9 twinax cables
Note on BF29: Duane L. Newhart x6378,3721,6378 11580N: 4 twinax
Note on BF30: Duane L. Newhart x6378,3721,6378 11580N: 16 twinax and 4 ethernet 4 gr58 for mps
Note on BF39: Duane L. Newhart x6378,3721,6378 11580N: total cable estimate for all 34 racks 100/racks. Moslty signal cables
Note on A40: Duane L. Newhart x6378,3721,6378 11580N: Everything on this line is an estimate/guess. Waiting on information from Cryo about the addition of these racks.
Note on J40: Fernanda G. Garcia x3798 13038N: Need to look into this and add info
Note on BF40: Duane L. Newhart x6378,3721,6378 11580N: Total Cable estimat for all 25 racks…types unknow
Note on AU42: Duane L. Newhart x6378,3721,6378 11580N: See Notes in last column
Note on L44: All 4 are for PUP systems main pumps
Note on L45: Duane L. Newhart x6378,3721,6378 11580N: May come with the RAW skid- check if RAW skid is accounted for. Smaller Rittel
Note on AL46: Changed to 3 rack and 208 at Tim Z request
Note on AE56: Jonathan W. Hunt x 15287N: Includes circulator and RF load
Note on AZ56: Duane L. Newhart x6378,3721,6378 11580N: HWR amps are mounted in the 4 racks.
Note on T57: Duane L. Newhart x6378,3721,6378 11580N: Estimate based on CMTF
Note on T58: Duane L. Newhart x6378,3721,6378 11580N: Estimate based on CMTF
Note on AH58: Fernanda G. Garcia x3798 13038N: Chiller WFE
Note on AE60: Jonathan W. Hunt x 15287N: Includes circulator and RF load
Note on AH60: Jonathan W. Hunt x 15287N: Changed per meeting with Jim Steimel on 11/15/18 PIP-II production RFPAs will have specs changed to 86
Note on L61: Jonathan W. Hunt x 15287N: Quantity covered under DN-019
Note on T62: Duane L. Newhart x6378,3721,6378 11580N: Estimate based on CMTF
Note on T63: Duane L. Newhart x6378,3721,6378 11580N: Estimate based on CMTF
Note on AE65: Jonathan W. Hunt x 15287N: Includes circulator and RF load
Note on AH65: Jonathan W. Hunt x 15287N: Changed per meeting with Jim Steimel on 11/15/18 PIP-II production RFPAs will have specs changed to 86
Note on L66: Jonathan W. Hunt x 15287N: Quantity covered under DN-023
Note on T67: Duane L. Newhart x6378,3721,6378 11580N: Estimate based on CMTF
Note on T68: Duane L. Newhart x6378,3721,6378 11580N: Estimate based on CMTF
Note on Q70: Fernanda G. Garcia x3798 13038N: verify with Curtis
Note on AE70: Jonathan W. Hunt x 15287N: Includes circulator and RF load
Note on AH70: Jonathan W. Hunt x 15287N: Changed per meeting with Jim Steimel on 11/15/18 PIP-II production RFPAs will have specs changed to 86
Note on L71: Jonathan W. Hunt x 15287N: Quantity covered under DN-027
Note on T72: Duane L. Newhart x6378,3721,6378 11580N: Estimate based on CMTF
Note on T73: Duane L. Newhart x6378,3721,6378 11580N:
Note on AE75: Jonathan W. Hunt x 15287N: Includes circulator and RF load
Note on AH75: Jonathan W. Hunt x 15287N: Changed per meeting with Jim Steimel on 11/15/18 PIP-II production RFPAs will have specs changed to 86
Note on L76: Jonathan W. Hunt x 15287N: Quantity covered under DN-031
Note on T77: Duane L. Newhart x6378,3721,6378 11580N: Estimate based on CMTF
Note on T78: Duane L. Newhart x6378,3721,6378 11580N: Estimate based on CMTF
Note on L95: Jonathan W. Hunt x 15287N: Quantity covered under DN-054
Note on L96: Jonathan W. Hunt x 15287N: Quantity covered under DN-054
Note on L97: Jonathan W. Hunt x 15287N: Quantity covered under DN-054
Note on L98: Jonathan W. Hunt x 15287N: Quantity covered under DN-054
Note on L99: Jonathan W. Hunt x 15287N: Quantity covered under DN-054
Note on L100: Jonathan W. Hunt x 15287N: Quantity covered under DN-054
Note on L103: Jonathan W. Hunt x 15287N: Quantity covered under DN-062
Note on L104: Jonathan W. Hunt x 15287N: Quantity covered under DN-062
Note on L105: Jonathan W. Hunt x 15287N: Quantity covered under DN-062
Note on L106: Jonathan W. Hunt x 15287N: Quantity covered under DN-062
Note on L107: Jonathan W. Hunt x 15287N: Quantity covered under DN-062
Note on L108: Jonathan W. Hunt x 15287N: Quantity covered under DN-062
Note on L110: Jonathan W. Hunt x 15287N: Quantity covered under DN-069
Note on L111: Jonathan W. Hunt x 15287N: Quantity covered under DN-069
Note on L112: Jonathan W. Hunt x 15287N: Quantity covered under DN-069
Note on L113: Jonathan W. Hunt x 15287N: Quantity covered under DN-069
Note on L114: Jonathan W. Hunt x 15287N: Quantity covered under DN-069
Note on L115: Jonathan W. Hunt x 15287N: Quantity covered under DN-069
Note on L117: Jonathan W. Hunt x 15287N: Quantity covered under DN-076
Note on L118: Jonathan W. Hunt x 15287N: Quantity covered under DN-076
Note on L119: Jonathan W. Hunt x 15287N: Quantity covered under DN-076
Note on L120: Jonathan W. Hunt x 15287N: Quantity covered under DN-076
Note on L121: Jonathan W. Hunt x 15287N: Quantity covered under DN-076
Note on L122: Jonathan W. Hunt x 15287N: Quantity covered under DN-076
Note on L124: Jonathan W. Hunt x 15287N: Quantity covered under DN-083
Note on L125: Jonathan W. Hunt x 15287N: Quantity covered under DN-083
Note on L126: Jonathan W. Hunt x 15287N: Quantity covered under DN-083
Note on L127: Jonathan W. Hunt x 15287N: Quantity covered under DN-083
Note on L128: Jonathan W. Hunt x 15287N: Quantity covered under DN-083
Note on L129: Jonathan W. Hunt x 15287N: Quantity covered under DN-083
Note on L132: Jonathan W. Hunt x 15287N: Quantity covered under DN-091
Note on L133: Jonathan W. Hunt x 15287N: Quantity covered under DN-091
Note on L134: Jonathan W. Hunt x 15287N: Quantity covered under DN-091
Note on L135: Jonathan W. Hunt x 15287N: Quantity covered under DN-091
Note on L136: Jonathan W. Hunt x 15287N: Quantity covered under DN-091
Note on L137: Jonathan W. Hunt x 15287N: Quantity covered under DN-091
Note on L139: Jonathan W. Hunt x 15287N: Quantity covered under DN-098
Note on L140: Jonathan W. Hunt x 15287N: Quantity covered under DN-098
Note on L141: Jonathan W. Hunt x 15287N: Quantity covered under DN-098
Note on L142: Jonathan W. Hunt x 15287N: Quantity covered under DN-098
Note on L143: Jonathan W. Hunt x 15287N: Quantity covered under DN-098
Note on L144: Jonathan W. Hunt x 15287N: Quantity covered under DN-098
Note on L146: Jonathan W. Hunt x 15287N: Quantity covered under DN-105
Note on L147: Jonathan W. Hunt x 15287N: Quantity covered under DN-105
Note on L148: Jonathan W. Hunt x 15287N: Quantity covered under DN-105
Note on L149: Jonathan W. Hunt x 15287N: Quantity covered under DN-105
Note on L150: Jonathan W. Hunt x 15287N: Quantity covered under DN-105
Note on L151: Jonathan W. Hunt x 15287N: Quantity covered under DN-105
Note on L153: Jonathan W. Hunt x 15287N: Quantity covered under DN-112
Note on L154: Jonathan W. Hunt x 15287N: Quantity covered under DN-112
Note on L155: Jonathan W. Hunt x 15287N: Quantity covered under DN-112
Note on L156: Jonathan W. Hunt x 15287N: Quantity covered under DN-112
Note on L157: Jonathan W. Hunt x 15287N: Quantity covered under DN-112
Note on L158: Jonathan W. Hunt x 15287N: Quantity covered under DN-112
Note on L160: Jonathan W. Hunt x 15287N: Quantity covered under DN-119
Note on L161: Jonathan W. Hunt x 15287N: Quantity covered under DN-119
Note on L162: Jonathan W. Hunt x 15287N: Quantity covered under DN-119
Note on L163: Jonathan W. Hunt x 15287N: Quantity covered under DN-119
Note on L164: Jonathan W. Hunt x 15287N: Quantity covered under DN-119
Note on L165: Jonathan W. Hunt x 15287N: Quantity covered under DN-119
Note on AG168: Jonathan W. Hunt x 15287N: Half in the gallery and half in the tunnel. I put the other half on DN-125
Note on AN168: Duane L. Newhart x6378,3721,6378 11580N: I summed the 65.4 amps @208V and the 38 amps @120V from the origional entries
Note on AG172: Jonathan W. Hunt x 15287N: See comment on DN-121
Note on AG175: Jonathan W. Hunt x 15287N: See comment on DN-126.1
Note on AG178: Jonathan W. Hunt x 15287N: Half in the gallery and half in the tunnel. I put the other half on DN-135
Note on AG182: Jonathan W. Hunt x 15287N: See comment on DN-151
Note on BF197: Duane L. Newhart x6378,3721,6378 11580N: C5 18 for Ion Gauges
Note on BF198: Duane L. Newhart x6378,3721,6378 11580N:
Note on L199: Fernanda G. Garcia x3798 13038N: Number of Controllers are set as one to one, but expect that to reduce.
Note on BF199: Duane L. Newhart x6378,3721,6378 11580N: Controllers need 1 power cable per unit
Note on BF200: Duane L. Newhart x6378,3721,6378 11580N: rack only have power and ethernet counted here. One of each per rack
Note on BF204: Duane L. Newhart x6378,3721,6378 11580N: C5 18 for Ion Gauges
Note on BF205: Duane L. Newhart x6378,3721,6378 11580N: RG58 Green for Pirani Gauges
Note on BF206: Duane L. Newhart x6378,3721,6378 11580N: Controllers need 1 power cable per unit
Note on BF207: Duane L. Newhart x6378,3721,6378 11580N: rack only have power and ethernet counted here. One of each per rack
Note on BF209: Duane L. Newhart x6378,3721,6378 11580N: 1 power cable 1 110v for fan if needed 1 controller cable so 3 cables per Turbo pump
Note on BF211: Duane L. Newhart x6378,3721,6378 11580N: C5 18 for Ion Gauges
Note on BF212: Duane L. Newhart x6378,3721,6378 11580N: rack only have power and ethernet counted here. One of each per rack
Note on BF217: Duane L. Newhart x6378,3721,6378 11580N: Controllers need 1 power cable per unit
Note on BF221: Duane L. Newhart x6378,3721,6378 11580N: rack only have power and ethernet counted here. One of each per rack
Note on BF226: Duane L. Newhart x6378,3721,6378 11580N: 1 power cable 1 110v for fan if needed 1 controller cable so 3 cables per Turbo pump
Note on BF229: Duane L. Newhart x6378,3721,6378 11580N: C5 18 for Ion Gauges
Note on BF230: Duane L. Newhart x6378,3721,6378 11580N: Controllers need 1 power cable per unit
Note on BF233: Duane L. Newhart x6378,3721,6378 11580N: 1 power cable 1 110v for fan if needed 1 controller cable so 3 cables per Turbo pump
Note on BF235: Duane L. Newhart x6378,3721,6378 11580N: C5 18 for Ion Gauges
Note on L236: Fernanda G. Garcia x3798 13038N: Checking to see if 4 are needed.
Note on BF236: Duane L. Newhart x6378,3721,6378 11580N: RG58 Green for Pirani Gauges
Note on BF237: Duane L. Newhart x6378,3721,6378 11580N: Controllers need 1 power cable per unit
Note on BF238: Duane L. Newhart x6378,3721,6378 11580N: rack only have power and ethernet counted here. One of each per rack
Note on BF240: Duane L. Newhart x6378,3721,6378 11580N: rack only have power and ethernet counted here. One of each per rack
Note on BF244: Duane L. Newhart x6378,3721,6378 11580N: C5 18 for Ion Gauges
Note on BF245: Duane L. Newhart x6378,3721,6378 11580N: RG58 Green for Pirani Gauges
Note on BF246: Duane L. Newhart x6378,3721,6378 11580N: Controllers need 1 power cable per unit
Note on L248: Jonathan W. Hunt x 15287N: Quantity covered under JH-001
Note on L250: Jonathan W. Hunt x 15287N: Quantity covered under JH-002
Note on L251: Jonathan W. Hunt x 15287N: Quantity covered under JH-003-A
Note on AE252: Jonathan W. Hunt x 15287N: Heat Load is captured under the Vane and Wall Cooling Skid components
Note on K254: Jonathan W. Hunt x 15287N: 3 + 1 standby spare. Space for 1 spare required
Note on L254: Jonathan W. Hunt x 15287N: Space for 1 spare required
Note on AE256: Jonathan W. Hunt x 15287N: This is the PIP-II LCW system total heat load. Refer to updated Pivot table for LCW system heat load
Note on AE259: Jonathan W. Hunt x 15287N: 24 KW heat load, but only one is running so I halved it for the calcs
Note on K260: Jonathan W. Hunt x 15287N: 1 + 1 standby spare. Space for 1 spare required
Note on L260: Jonathan W. Hunt x 15287N: Space for 1 spare required
Note on K262: Jonathan W. Hunt x 15287N: 1 + 1 standby spare. Space for 1 spare required
Note on L262: Jonathan W. Hunt x 15287N: Space for 1 spare required
Note on L269: Jonathan W. Hunt x 15287N: Quantity covered in JH-018
Note on AE285: Jonathan W. Hunt x 15287N: Includes circulator and RF loads
Note on AH300: Fernanda G. Garcia x3798 13038N: original PIP2IT circulators used 83. Need to change to 86 for PIP2
Note on AC304: Jonathan W. Hunt x 15287N: This is not a dedicated supply line, just ambient from the tunnel
Note on AD304: Jonathan W. Hunt x 15287N: can this be cooled by LCW? No, most likely this will be air cooled
Note on AE304: Jonathan W. Hunt x 15287N: Information not available from Vendor. Placeholder based on power in. See notes section
Note on AC305: Jonathan W. Hunt x 15287N: This is not a dedicated supply line, just ambient from the tunnel
Note on AE305: Jonathan W. Hunt x 15287N: Information not available from Vendor. Placeholder based on power in. See notes section
Note on AG306: Fernanda G. Garcia x3798 13038N: Heat load to air from HWR cryo couplers not cables
Note on AD315: Fernanda G. Garcia x3798 13038N: 60 gpm for entire cold box station at 60 deg F or higher
Note on AE315: Jonathan W. Hunt x 15287N: Refer to supply temperature and flow rate information provided
Note on AN326: Jonathan W. Hunt x 15287N: Per Review Notes document dated 11-14-18
Note on AN328: Jonathan W. Hunt x 15287N: Per Review Notes document dated 11-14-18
Note on AN330: Jonathan W. Hunt x 15287N: Per Review Notes document dated 11-14-18
Note on AN333: Jonathan W. Hunt x 15287N: Per Review Notes document dated 11-14-18
Note on AN334: Jonathan W. Hunt x 15287N: Per Review Notes document dated 11-14-18
Note on L343: Fernanda G. Garcia x3798 13038N: 1 of these is for ODH interlocks

## Dropdown Lists
Dropdown List Tables
WBS Names and IDs |  |  | General |  | Space Designations |  | Level of Design | Uncertainty Multipliers |  |  | Source of Requirements | Uncertainty Multipliers
HWR | 121.2.02 |  | Yes |  | HBB-Lower High Bay |  | Pre-conceptual | 100% |  |  | Off the Shelf | 5%
SSR | 121.2.03 |  | No |  | HBB-Upper High Bay |  | Conceptual | 50% |  |  | Prototype-Testing | 25%
LBHB | 121.2.04 |  | TBD |  | HBB-Control Room |  | Preliminary | 30% |  |  | Expert Opinion | 50%
CP | 121.2.05 |  | N/A |  | HBB-Tech Support Space |  | Final | 15% |  |  | Completely Unknown | 100%
CDS | 121.2.06 |  |  |  | HBB-Computer Space
HPRF | 121.3.03 |  | None |  | HBB-Mechanical/Electrical Space
LLRF | 121.3.04 |  | N/A |  | HBB-Exterior Space
Magnets | 121.3.05 |  | Other |  | LT-HWR
Vacuum | 121.3.06 |  |  |  | LT-SSR1
Controls | 121.3.07 |  | Floor |  | LT-SSR2
SS | 121.3.08 |  | Suspended |  | LT-LB650
Instrumentation | 121.3.09 |  | Rack Mounted |  | LT-HB650
WFE | 121.4.02 |  | Beamline/Tunnel |  | LG-General
BldgI | 121.4.03 |  |  |  | LG-HWR
BeamCommissioning | 121.4.04 |  |  |  | LG-SSR1
RingsInst | 121.5.05 |  |  |  | LG-SSR2
BTLBAL | 121.5.04 |  |  |  | LG-LB650
LG-HB650
WBS Names and IDs | Level 2 |  |  |  | LG-BTL Power Supply
HWR | 121.2 |  |  |  | LG-Exterior Space
SSR | 121.2 |  |  |  | BTL-Beamline Tunnel
LBHB | 121.2 |  |  |  | BAL-Beam Asborber Space
CP | 121.2 |  |  |  | BTL-Muon Campus Stub
CDS | 121.2 |  |  |  | Cryoplant Building
HPRF | 121.3 |  |  |  | PUB
LLRF | 121.3 |  |  |  | Booster
Magnets | 121.3
Vacuum | 121.3
Controls | 121.3
SS | 121.3
Instrumentation | 121.3
WFE | 121.4
BldgI | 121.4
BeamComissioning | 121.4
RingsInst | 121.5
BTLBAL | 121.5
Sub-Tier Systems
HPRF | LLRF | Magnets | Vacuum | Controls | SS | Instrumentation | BTLBAL | WFE | BldgI | HWR | SSR | LBHB | CP | CDS | RingsInst
HB650 | Buncher | Chopper Kicker | WFE | Computers, Center Service | Interlocks | BLM | Collimator Controls | Ion Source | Compressed Air | HWR Cryomodule | SSR1 | LB650 | Cold Box Station | General Data Acquisition
HWR | HB650 | Fast Dipole Switch | HB650 | Computers, Console | Interlocks, SSIU | BPM | RAW Absorber | LEBT | Dissolved Oxygen | Vacuum, Cavity | SSR2 | HB650 | Network Room | HWR
LB650 | HWR | Magnets, C-dipole | HWR | Computers, Front End | ODH | General Instrumentation |  | MEBT | LCW | Vacuum, Insulating |  |  | Warm Compressor Section | SSR1
MEBT Buncher Cavity | LB650 | Magnets, Dipole | Insulating Vac | Diagnostic Room |  | Laser Wire |  | RFQ | Resistivity Control |  |  |  |  | SSR2
RFQ | Primary Reference Line | Magnets, Dipole Corrector | Ion Pump PS System | Fiber Distribution |  | MW |  | WFE | Reverse Osmosis |  |  |  |  | LB650
SSR1 | RF Interlocks | Magnets, Large Bore | SRF | General Data Acquisition |  | RWC |  |  | RFQ |  |  |  |  | HB650
SSR2 | RFQ | Magnets, Regular Quadrupole | SSR | Laser Transport |  | Toroid |  |  | Utility Nitrogen
| SSR1 | Magnets, Septum | BTL/BAL | Motor Controllers |  | Wire Scanner
| SSR2 | Magnets, Skew Quadrupole |  | PLC/LCW Controls
|  | Magnets, Sweep |  | RAW System
|  | Magnets, Switch |  | RFQ
|  | Solenoids |  | Timing System
Components
HPRF | LLRF | Magnets | Vacuum | Controls | SS | Instrumentation | BTLBAL | WFE | BldgI | HWR | SSR | LBHB | CP | CDS | RingsInst
Cavities | 162.5 LLRF Hardware | Cables | Controller, Ion Pump | Alarms | Critical Device Controller | Laser Room | Magnets | Absorber Assembly | Air Compressor | Couplers | Couplers | Couplers | 4.5K Cold Box | Cryomodule
Circulators | 325 LLRF Hardware | Magnets | Controller, Ion/Pirani Gauge | Console Computers | Interlock Box | Racks | Power Supplies | Allison Scanner | Bottles | Cryomodule | Cryomodule | Cryomodule | Cold Box Equipment | Racks
Flow Monitors | 650 LLRF Hardware | Power Supplies | Controller, Turbo Pump | Consoles, Fixed | Interlock Gates |  | Pumps | Beamline | Dewar | Pumps and Controllers |  |  | Compressors
Interlocks | Power Supplies | Racks | Gate Valves | Consoles, Mobile | ODH Monitor |  | Racks | Bottle Enclosure | Dryer |  |  |  | Entire Area
Power Amplifiers | Racks |  | Gauges, Ion | Other Hardware Devices | Rack Mount |  |  | Bunching Cavities | Filter |  |  |  | Generator
Power Supplies | Resonance Control |  | Gauges, Pirani | Racks | Racks |  |  | Cabinets | Heat Exchanger |  |  |  | Panels
Racks |  |  | NEG |  |  |  |  | Chiller | Pump |  |  |  | Racks
Reflected Power Loads |  |  | NEG Controller |  |  |  |  | Chopper | Skids |  |  |  | Skids
|  |  | Power Supply |  |  |  |  | Circulators | Strainer |  |  |  | Storage Tank
|  |  | Pump, Ion |  |  |  |  | Controllers | Tank |  |  |  | Welding Receptacle
|  |  | Pump, Roughing |  |  |  |  | Couplers | Water/Oil Separator
|  |  | Pump, Turbo |  |  |  |  | Ion Source
|  |  | Racks |  |  |  |  | Kickers
|  |  | Valves |  |  |  |  | Magnets
Panels
Power Amplifiers
Power Supplies
Racks |  |  |  |  | Cooling |  |  | Racks
Size | Front Access | Closed Sides | Rear |  | Air, Compressed |  |  | Scrapers Vacuum Chamber
Other | Doors | Left AND Right | Closed |  | Air, Environment |  |  | Skids
19"W/52U X 29" D | Open | Left Only | Open |  | Chilled LCW |  |  | Solenoids
19"W/60U X 29" D |  | Open | Door |  | Chilled Water |  |  | Vanes
4'W x 6'H x 3'D |  | Right Only |  |  | ICW |  |  | Walls
TBD |  |  |  |  | LCW
Power to Rack |  | Breaker (A) |  |  | Cable Types
120 V - 1 Phase - 2 Wire |  | 15 |  |  | Flexible <1cm (e.g. RG58)
208 V - 1 Phase - 2 Wire |  | 20 |  |  | "Flexible" >1cm (e.g. 500MCM stranded)
240 V - 1 Phase - 2 Wire |  | 30 |  |  | Semi rigid <1cm (e.g. 0.25" Heliax)
208 V - 3 Phase - 3 Wire |  | 40 |  |  | Semi-rigid >1cm (e.g. 0.5" Heliax)
480 V - 3 Phase - 3 Wire |  | 50 |  |  | Rigid (e.g. hardline coax)
208Y/120 V - 3 Phase - 4 Wire |  | 60
480Y/277 V - 3 Phase - 4 Wire |  | 120
Other (specify) |  | 125
TBD |  | 200
240
Communication |  | 450
Ethernet |  | Other
ACNET |  | TBD
WIFI
Other (specify) |  | Floors
TBD |  | Bare concrete
Sealed concrete
Disclaimer: | amplifiers at 2mA. CW RF, specify the amplifiers to accelrate 2MW of beam in the cavities