## Slide 1: ODH Calculation Plans
ND cavern ODH calculations have not been performed, yet.
A preliminary design guidance could be based on the MicroBooNE ventilation system. MicroBooNE is a 90 ton LAr detector. The MicroBooNE pit footprint (floor area) is around eight times smaller than the ND cavern.
MicroBooNE Ventilation Parameters
  Duct Size: 3 ft diam.
  Louver Locations: top and bottom for LHe and LAr
  Ventilation Speed: 7,500 ft3/min with two fans for redundancy
Initial ODH scoping calculation will require a few weeks of a cognizant engineer.
A full study can later be performed once the designs are more matured.