## Slide 1: Detector Grounding
T. Shaw
FNAL
20 AUG 2019

## Slide 2: Detector Grounding
Are there compromises we can make on Infrastructure Grounding plan to reduce cost?

## Slide 3
EDMS 2095975

## Slide 6
From Jack – distance between Cryostat wall and Cavern “Minimally it is supposed to be 430 mm”
Area of cryostat side wall 17.84 x 65.84 = 1176 sq. meters

## Slide 7: Calculate the capacitance between Cryostat and Building/Cavern Ground
Consider putting wire mesh on cavern wall parallel to cryostat instead of non-conductive shotcrete.
Assume parallel plate capacitor formed between cryostat and Cavern wall which contain wire mesh; not exactly the case but fringe effects help to approximate model; provides worst case number
C = 24 nF for one side of cryostat, Ctot = 48 nF both sides
Xc = 1/(2πfC)
  @ 2MHz = 1.7 ohms
  @500Khz = 6.65 ohms
For building noise not to couple onto detector, impedance back to building earth ground should be << ~1.7 ohms.
NOTE – Calculated Capacitance is likely much lower due to the fact wire mesh was approximated as plate. If calculated capacitance is 10% of above
  @ 2MHz = 17 ohms
  @500Khz = 66.5 ohms

## Slide 8: Building/Cavern Ground to remote Earth < 1 ohm
Conclusion: By design, any noise on the cavern walls shall have a very low impedance path to remote earth ground and will be less likely to couple onto the Cryostat and Detector ground. We can consider elimination of requirement for non-conductive shotcrete of walls parallel to the cryostat.

## Slide 9: Cost savings if we allow wire mesh on cavern walls parallel to detector
Doug provided a quick estimate of potential cost savings if we allow a continuation of wire mesh on the cavern walls parallel to the cryostat.
From email communication 8/5/2019
  Eliminate shotcrete from detector cavern walls, elev. 4850L to 4910L,
  116,966 SF
  Add WWF mesh on the detector cavern walls, elev. 4850L to 4910L,
  108,405 SF

## Slide 10: Cost savings if we allow wire mesh on cavern walls parallel to detector
Shotcrete $1,289.41/CY (Material cost of $927.16/CY and placement cost of $362.25/CY)
KAJV had a waste factor of 2.24 for shotcrete. That equates to 36.5 SF/CY,
or a unit price of $35.31/SF for shotcrete
WWF $17.66/SF (Material cost of $1.05/SF and install cost of $16.61/SF)
Based on these numbers, the change would be:
  Deduct 116,966 SF x $35.31/SF = ($4,130,069)
  Add 108,405 SF x $17.66/SF = $1,914,432
  Total Credit ($2,215,637)
So about $1M savings per detector cavern if we eliminated shotcrete and added WWF on the walls from 4850 to 4910.