## Slide 2: ICARUS 3d Simulations
Diego Zambelli - CERN EN-HE
Julia Laast– CERN EN-CV, CFD team

## Slide 3: Scope and CFD study structure
The scope of this project is to determine the Temperature and air Velocity distribution within the 3d geometry of the Icarus building.
The input geometry will be simplified, executing CFD simulations including all heat sources.
Input
Simplified 3d Geometry
Post-processing
and Results
Calculation
Meshing
Input
Boundary conditions and heat fluxes
Geometrical Model
fluid body

## Slide 4: 2D Simulation
Negligible thermal effects in small gaps, only global phenomena have been investigated

## Slide 5: 2D Simulation
Based on the 2D results, the global temperature distribution has to be investigated further

## Slide 6: Geometry 3d Geometry
Top view
Paneling system
Bottom view

## Slide 7: Geometry Simplified 3d Geometry
Main changes:
Merging of minicrates
Elimination of long cryogenic pipes and foot panels
Merging of cosmic ray panels with vessel except upper panels
Top view
Paneling system
Bottom view

## Slide 8: Geometrical model

## Slide 9: Component heat fluxes (as provided by Fermilab)
Zero heat flux components:
Cryogenic elements
Vessel Racks
Building
Negative Vessel heat flux
Component | Area (m2) | Power (W) | Heat Flux (W/m2)
Minicrates |  |  | 
Minicrates west | 57.7873 | 3750 | 64.89315126
Minicrates east | 57.7873 | 3750 | 64.89315126
Minicrates c_west | 57.7873 | 3750 | 64.89315126
Minicrates c_east | 57.7873 | 3750 | 64.89315126
Cryogenic |  |  | 
Cryogenic 1 | 22.3153 | 0 | 0
Cryogenic 2 | 13.4303 | 0 | 0
Cryogenic 3 | 13.4303 | 0 | 0
Cryogenic 4 | 10.1316 | 0 | 0
Cryogenic 5 | 13.2827 | 0 | 0
Cryogenic 6 | 15.7551 | 0 | 0
Cryogenic 7 | 10.1316 | 0 | 0
Cryogenic 8 | 20.7131 | 0 | 0
Cryogenic 9 | 13.4303 | 0 | 0
Cryogenic 10 | 5.596 | 0 | 0
Cryogenic 11 | 5.596 | 0 | 0
Building | 3160.5182 | 0 | 0
Racks |  |  | 
Racks_south | 10.868 | 0 | 0
Racks_north | 10.868 | 0 | 0
Racks_nwest | 26.129 | 3333.333333 | 127.572174
Racks_west | 33.589 | 3333.333333 | 99.23883811
Racks_swest | 26.129 | 3333.333333 | 127.572174
Racks_neast | 33.759 | 7500 | 222.1629788
Racks_seast | 10.868 | 7500 | 690.0993743
Cosmic Rays panel |  |  | 
Panel 1 | 45.4996 | 227.498 | 5
Panel 2 | 607.8 | 3039 | 5
Air supply pipeline |  |  | 
Pipe_west | 58.8528 | 0 | 0
Pipe_east | 58.8528 | 0 | 0
inlet_ext_north 1 | 0.7222 | 0 | 0
inlet_ext_nwest | 0.7222 | 0 | 0
inlet_ext_west | 0.7222 | 0 | 0
inlet_ext_swest | 0.7222 | 0 | 0
inlet_ext_north 2 | 0.7222 | 0 | 0
inlet_ext_neast | 0.7222 | 0 | 0
inlet_ext_east | 0.7222 | 0 | 0
inlet_ext_east | 0.7222 | 0 | 0
inlet_ext_seast | 0.7222 | 0 | 0
inlet_int_north1 | 1.2333 | 0 | 0
inlet_int_nwest | 1.2333 | 0 | 0
inlet_int_west | 1.2333 | 0 | 0
inlet_int_swest | 1.2333 | 0 | 0
inlet_int_north2 | 1.2333 | 0 | 0
inlet_int_neast | 1.2333 | 0 | 0
inlet_int_east | 1.2333 | 0 | 0
inlet_int_seast | 1.2333 | 0 | 0
Vessel_racks |  |  | 
Vracks_north1 | 4.5472 | 0 | 0
Vracks_north2 | 4.5472 | 0 | 0
Vracks_north3 | 4.5472 | 0 | 0
Vracks_north4 | 4.5472 | 0 | 0
Vracks_center1 | 5.04 | 0 | 0
Vracks_center2 | 3.1072 | 0 | 0
Vracks_south1 | 4.5472 | 0 | 0
Vracks_south2 | 4.5472 | 0 | 0
Vracks_south3 | 4.5472 | 0 | 0
Vracks_south4 | 4.5472 | 0 | 0

## Slide 10: Results
Simulations including Vessels, mini-crates, racks and upper panel heat fluxes have been performed.
Temperature and air velocity distribution are represented in the following slides

## Slide 11: Global Temperature distribution
55 C
19 C
43 C
39 C

## Slide 12: Temperature distribution Side View

## Slide 13: Temperature distribution Frontal View

## Slide 14: Air velocity distribution

## Slide 15: Air velocity distribution Frontal View

## Slide 16: Conclusions
Critical points have been identified in which temperatures are exeeding thresholds:
Between tagger and concrete blocks.
Underneath the tagger roof.
Possible mitigation solutions:
Better air velocity distribution.
Local cooling system.
We could calculate in the frame of the present simulation such solutions.

## Slide 17: Possible recommendations
  Create a more uniform temperature distribution by conveying air into poorly ventilated upper regions
  Introduce Cooling units

## Slide 18: Thank you for your attention!
Diego Zambelli & Julia Laast, CFD Team, CERN, www.cern.ch/cfd