## Power Supplies
PIP II QUAD MAGNET POWER SUPPLIES
|  |  |  | Ramp Cycle Time: | 10000 |  |  |  | Cabling Assumptions: | [17 empty] | Power Supply Assumptions:
[10 empty] | M&S |  |  | Install | [15 empty] | Power Supply Loses = | 10% | of Load losses
[9 empty] | 500 kcmil: | 7.2 | per ft |  | 3.61 | per ft | [14 empty] | Power Supply PF = | 0.9 | for SM PSs
[9 empty] | 1/0 AWG | 1.4 | per ft |  | 1.12 | per ft | [14 empty] | Power Supply PF = | (Voperating/Vmax) for SCR PSs
|  |  | Might take 4 magnets out of 14-1 and 13-1 and | [25 empty] | Cost/watt for SM Power Supply = | See Calc | $/watt
|  |  | put them on separate supplies (Beam tuning) | [25 empty] | Cost/watt for SCR Power Supply = | 0.64 | $/watt
Might take 2 magnets out of 11-1 and 11-2 and
put them on seprate supplies (Beam defocusing
for dump instead of sweaping magnet)
|  | MAGNET LOAD | [6 empty] | LOAD CABLING | [8 empty] | LOAD CHARACTERISTICS | [14 empty] | POWER SUPPLY | [9 empty] | OTHER ITEMS | [5 empty] | FEEDERS
CIRCUIT | Number | MAGNET | Beamline | MAGNET | # | MAG. | MAG. |  | Cable Type | # of cables 1 way | R/kFt | L 1-way | Cable RES. | Cable Costs |  |  |  | Total Circuit Res. | Peak Current | Min. Current | dI/dT | Peak VOLT. | RMS CURR. | Peak Power |  | PS Location | PS TYPE | Max. Volt | Max. Curr. | PS Rating | Losses |  | Power Supply Costs |  |  |  | PS Installation Costs | [5 empty] | High Regulation | Quench Protection |  |  |  |  | AVE PWR | kVA | Amps
NAME | of Circuits | TYPE | Location & Distance along beamline (ft) | MODEL | MAGs | IND. | RES. |  |  |  | ohms | (ft) | ohms | M&S ($k) | Install ($k) | Tot. Cir ($k) |  | ohms | (amps) | (amps) | (A/s) | (volts) | (amps) | (kW) |  |  | SM or SCR | (volts) | (amps) | (kW) | (kW) | # | M&S ($k) | Tech. Labor (hrs) | Eng. Labor (hrs) |  | M&S ($k) | Tech. Labor (hrs) | Eng. Labor (hrs) | Elect. Labor (hrs) |  |  | M&S ($k) | M&S ($k) | Tech. Labor (hrs) | Eng. Labor (hrs) | SM V% | SM I % | (kW) | kVA | I
QD Arc1 | 1 | 100A |  | BTLQ-100A | 11 | 0.00874 | 0.045 |  | 1/0 | 1 | 0.122 | 809 | 0.1974 | 2.2652 | 1.8122 | 4.0774 |  | 0.6924 | 100 | 100 | 0 | 69.2396 | 100 | 6.924 |  |  | SM | 80 | 125 | 10 | 0.8 | 1 | 13.2085 | 148 | 28 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 86.5495 | 80 | 7.724 | 8.5822 | 10.335
QF Arc1 | 1 | 100A |  | BTLQ-100A | 10 | 0.00874 | 0.045 |  | 1/0 | 1 | 0.122 | 790 | 0.19276 | 2.212 | 1.7696 | 3.9816 |  | 0.64276 | 100 | 100 | 0 | 64.276 | 100 | 6.4276 |  |  | SM | 80 | 125 | 10 | 0.8 | 1 | 13.2085 | 148 | 28 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 80.345 | 80 | 7.2276 | 8.0307 | 9.6708
QD Dump | 1 | 100A |  | BTLQ-100A | 2 | 0.00874 | 0.045 |  | 1/0 | 1 | 0.122 | 397 | 0.096868 | 1.1116 | 0.88928 | 2.0009 |  | 0.18687 | 100 | 100 | 0 | 18.6868 | 100 | 1.8687 |  |  | SM | 40 | 125 | 5 | 0.4 | 1 | 10.9159 | 148 | 28 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 46.717 | 80 | 2.2687 | 2.5208 | 3.0356
QF Dump | 1 | 100A |  | BTLQ-100A | 2 | 0.00874 | 0.045 |  | 1/0 | 1 | 0.122 | 397 | 0.096868 | 1.1116 | 0.88928 | 2.0009 |  | 0.18687 | 100 | 100 | 0 | 18.6868 | 100 | 1.8687 |  |  | SM | 40 | 125 | 5 | 0.4 | 1 | 10.9159 | 148 | 28 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 46.717 | 80 | 2.2687 | 2.5208 | 3.0356
QD Arc 2 | 1 | 100A |  | BTLQ-100A | 11 | 0.00874 | 0.045 |  | 1/0 | 1 | 0.122 | 903 | 0.22033 | 2.5284 | 2.0227 | 4.5511 |  | 0.71533 | 100 | 100 | 0 | 71.5332 | 100 | 7.1533 |  |  | SM | 80 | 125 | 10 | 0.8 | 1 | 13.2085 | 148 | 28 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 89.4165 | 80 | 7.9533 | 8.837 | 10.6419
QD Fine 1 | 1 | 100A | End of Arc 2 | BTLQ-100A | 1 | 0.00874 | 0.045 |  | 1/0 | 1 | 0.122 | 855 | 0.20862 | 2.394 | 1.9152 | 4.3092 |  | 0.25362 | 100 | 100 | 0 | 25.362 | 100 | 2.5362 |  |  | SM | 40 | 125 | 5 | 0.4 | 1 | 10.9159 | 148 | 28 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 63.405 | 80 | 2.9362 | 3.2624 | 3.9288
QF Arc 2 | 1 | 100A |  | BTLQ-100A | 11 | 0.00874 | 0.045 |  | 1/0 | 1 | 0.122 | 876 | 0.21374 | 2.4528 | 1.9622 | 4.415 |  | 0.70874 | 100 | 100 | 0 | 70.8744 | 100 | 7.0874 |  |  | SM | 80 | 125 | 10 | 0.8 | 1 | 13.2085 | 148 | 28 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 88.593 | 80 | 7.8874 | 8.7638 | 10.5537
QF Fine 1 | 1 | 100A | End of Arc 2 | BTLQ-100A | 1 | 0.00874 | 0.045 |  | 1/0 | 1 | 0.122 | 855 | 0.20862 | 2.394 | 1.9152 | 4.3092 |  | 0.25362 | 100 | 100 | 0 | 25.362 | 100 | 2.5362 |  |  | SM | 40 | 125 | 5 | 0.4 | 1 | 10.9159 | 148 | 28 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 63.405 | 80 | 2.9362 | 3.2624 | 3.9288
QD Large Bore | 1 | 100A | ` | BTLQ-100A | 1 | 0.00874 | 0.045 |  | 1/0 | 1 | 0.122 | 388 | 0.094672 | 1.0864 | 0.86912 | 1.9555 |  | 0.13967 | 100 | 100 | 0 | 13.9672 | 100 | 1.3967 |  |  | SM | 20 | 165 | 3.3 | 0.2 | 1 | 9.9307 | 148 | 28 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 69.836 | 60.6061 | 1.5967 | 1.7741 | 2.1365
QF Large Bore | 1 | 100A |  | BTLQ-100A | 1 | 0.00874 | 0.045 |  | 1/0 | 1 | 0.122 | 368 | 0.089792 | 1.0304 | 0.82432 | 1.8547 |  | 0.13479 | 100 | 100 | 0 | 13.4792 | 100 | 1.3479 |  |  | SM | 20 | 165 | 3.3 | 0.2 | 1 | 9.9307 | 148 | 28 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 67.396 | 60.6061 | 1.5479 | 1.7199 | 2.0712
EOL Quad | 6 | 100A | Powered from Booster | BTLQ-100A | 1 | 0.00874 | 0.045 |  | 1/0 | 1 | 0.122 | 100 | 0.0244 | 0.28 | 0.224 | 0.504 |  | 0.0694 | 150 | 150 | 0 | 10.41 | 150 | 1.5615 |  |  | SM | 15 | 220 | 3.3 | 0.225 | 6 | 59.5844 | 362.5245 | 68.5857 |  | 6 | 48 | 36 | 90 |  |  | 9.3 |  |  |  | 69.4 | 68.1818 | 1.7865 | 1.985 | 2.3904
|  |  | Most power supplies are in F3 except noted!!! |  | 52
EOL quads are 3 doublets, 2 in Booster and 1 before the chute in the BTL
# of Circuits | 16 | [12 empty] | 2.2652 | 11.2605 | 25.3361 | [32 empty] | 46.1332 | 51.2591 | 61.7282
[33 empty] | 2010 Cost | [9 empty] | 2010 Cost
[15 empty] | TOTAL CABLE COSTS ($k): | 33.9595 | [6 empty] | Total Peak Power: | 40.7082 | kW | [6 empty] | TOTAL PS COSTS, M&S ($k): | 175.9435 | [8 empty] | REGULATION INCREASE, M&S ($k): | 24.8
[34 empty] | Tech | Eng | [13 empty] | TOTAL M&S: | 191.9435 | 2018 $$
[5 empty] | NOTES: | [27 empty] | Total PS Labor (hrs): | 1842.5245 | 348.5857 | [13 empty] | TOTAL LABOR: | Tech | Eng.
|  |  |  | * | Costs do not include cable tray in buildings, tunnels, cost of penetrations or load cable installation. | [27 empty] | (man-months): | 11.5158 | 2.1787 | [8 empty] | TOTAL QUENCH PROTECTION, M&S ($k): | 0 |  |  |  | MAN-HOURS | 1970.5245 | 444.5857
|  |  |  | * | M&S COSTS BASED ON 2018 | [30 empty] | Total PS Installation Costs, M&S ($k): | 16 | [10 empty] | TOTAL M&S |  | 191.9435
[38 empty] | Tech | Eng. | Elect. |  |  |  |  | Tech | Eng. |  | 2018 $$
|  |  |  | * | M&S savings based on number of units were not applied to "Power Supply Costs" or "High Regulation" - this is our experience | [31 empty] | Total PS Installation Labor (hrs): | 128 | 96 | 240 |  |  |  | Quench Prot. Labor (hrs): | 0 | 0
[37 empty] | (man-months): | 0.8 | 0.6 | 1.5 |  |  |  | (man-months): | 0 | 0
|  |  | 4-Quadrant Switch Mode PS Costs | [6 empty] | BASIC POWER SUPPLY COSTS | [6 empty] | For a single Power System, Rack and Filter | [8 empty] | For a Single power supply +/- 300 ppm regulation: | [8 empty] | For a Single power supply +/- 100 ppm regulation:
|  |  | M&S COSTS | $k | kW |  |  | SM POWER SUPPLY QUOTES | [8 empty] | 480 VAC Contrls | 1.3 | 1 | 1.3 | 2018 |  |  |  |  | LEM (1 kamp) | 0.3 | 1 | 0.3 | 2018 | [6 empty] | DCCT (1kamp) | 1.6 | 1 | 1.6 | 2018
|  |  | Ferm-built 65amp/150volt | [5 empty] | Manufacturer | Volts | Amps | Power | Cost | $/watt |  |  | Inductors | 0 | 0 | 0 | Eng Estimate |  |  |  |  | DAC | 0.2 | 1 | 0.2 | 2018 | [6 empty] | DAC | 0.2 | 1 | 0.2 | 2018
|  |  | 10kW | 4 | 10 | [6 empty] | (kW) | $k |  |  |  | Caps and Res. | 0 | 0 | 0 | Eng Estimate |  |  |  |  | DAC Card | 0.4 | 1 | 0.4 | 2018 | [6 empty] | DAC Card | 0.5 | 1 | 0.5 | 2018
|  |  | Raw power Supply | 5 | 22 |  |  |  | Magna-Power | 20 | 1000 | 20 | 11.8 | 0.59 |  |  |  |  | Subtotal: |  | 1.3 | ($k) |  |  |  | PC104 | 1 | 1 | 1 | 2018 | [6 empty] | PC104 | 1 | 1 | 1 | 2018
[9 empty] | Magna-Power | 32 | 750 | 24 | 14 | 0.58333 | [11 empty] | PLC | 1.4 | 1 | 1.4 | 2018 | [6 empty] | PLC | 1.4 | 1 | 1.4 | 2018
|  |  | LABOR | Tech |  |  |  |  | Magna-Power | 40 | 625 | 25 | 14 | 0.56 |  |  | Electrician | 1.2 | 1 | 1.2 | 15 | m-hrs |  |  |  | Reg. Chassis | 0.5 | 1 | 0.5 | 2018 | [6 empty] | Reg. Chassis | 0.5 | 1 | 0.5 | 2018
|  |  | SM Units | 3 | hrs |  |  |  | Magna-Power | 40 | 750 | 30 | 16.4 | 0.54667 |  |  | Power supply | 14 | 1 | 14 | 2018 |  |  |  |  | PS Int. Chassis | 0.5 | 1 | 0.5 | 2018 | [6 empty] | PS Int. Chassis | 0.5 | 1 | 0.5 | 2018
|  |  | Raw PSs and Rack | 50 | hrs |  |  |  | Sorenson (SG) | 40 | 375 | 15 | 9.3 | 0.62 |  |  | Rack | 2.5 | 1 | 2.5 | 2018 |  |  |  |  | LVPSs | 0.15 | 3 | 0.45 | 2018 | [6 empty] | LVPSs | 0.15 | 4 | 0.6 | 2018
|  |  |  | Eng |  |  |  |  | Lambda (GEN) | 40 | 250 | 10 | 5.8 | 0.58 |  |  |  |  | TOTAL: | 19 | ($k) |  |  |  |  | Back Plane | 0.2 | 1 | 0.2 | Engineering Estimate | [6 empty] | Back Plane | 0.2 | 1 | 0.2 | Engineering Estimate
|  |  | SM Units | 3 | hrs |  |  |  |  | Not used |  | See Calc Tab
|  |  | Design, layout, Raw PS | 20 | hrs |  | PHASE CONTROLLED (SCR) POWER SUPPLY COSTS | [11 empty] | LABOR | Tech | Eng | [6 empty] | Total: | 4.95 | ($k) | [8 empty] | Total (M&S): | 6.5 | ($k)
[9 empty] | Manufacturer: | votls | Amps | Power | Cost | $/watt |  |  |  |  | Assembly: | 1.5 | 0.2 | man-weeks
[12 empty] | (kw) | $k | [5 empty] | Testing: | 0.2 | 0.1 | man-weeks | [6 empty] | LABOR | Tech | Eng | [7 empty] | LABOR | Tech | Eng
[9 empty] | Spang: | 75 | 1000 | 75 | 48 | 0.64 | [14 empty] | Assembly: | 1.5 | 0.2 | man-weeks | [6 empty] | Assembly: | 1.5 | 0.2 | man-weeks
[9 empty] | 2018 | 150 | 500 | 75 | 48 | 0.64 | [14 empty] | Testing: | 0.5 | 0.2 | man-weeks | [6 empty] | Testing: | 0.5 | 0.2 | man-weeks
[29 empty] | Installation | 0.2 | 0.15 | man-weeks | [6 empty] | Installation | 0.2 | 0.2 | man-weeks
[10 empty] | V/I Regulator : | 5 | $k ea | 2018
(Fermi designed and built)
Note on N4: From the 2013 NEC Cost book via Ryan Crawford
Note on AD52: This supply is at the 80% limit

## $ per W Calc
Lambda Web Prices 5-21-19
Power(kW) | Price(k$) | $/kW | Calculation(k$)
0.75 | 1.604 | 2.1387 | 1.6181
1.5 | 1.915 | 1.2767 | 2.3633
2.4 | 2.902 | 1.2092 | 3.0738
3.3 | 3.698 | 1.1206 | 3.6807
5 | 4.612 | 0.9224 | 4.6659
10 | 6.618 | 0.6618 | 6.9585
15 | 8.873 | 0.59153 | 8.8066
Calculation Equation
(1.740.8*X^0.5823)+150