## Power Supplies
PIP II QUAD MAGNET POWER SUPPLIES
|  |  |  | Ramp Cycle Time: | 10000 |  |  |  | Cabling Assumptions: | [17 empty] | Power Supply Assumptions:
[10 empty] | M&S |  |  | Install | [15 empty] | Power Supply Loses = | 10% | of Load losses
[9 empty] | 500 kcmil: | 7.2 | per ft |  | 3.61 | per ft | [14 empty] | Power Supply PF = | 0.9 | for SM PSs
[9 empty] | 1/0 AWG | 1.4 | per ft |  | 1.12 | per ft | [14 empty] | Power Supply PF = | (Voperating/Vmax) for SCR PSs
[29 empty] | Cost/watt for SM Power Supply = | See Calc | $/watt
[29 empty] | Cost/watt for SCR Power Supply = | 0.64 | $/watt
|  | MAGNET LOAD | [6 empty] | LOAD CABLING | [8 empty] | LOAD CHARACTERISTICS | [14 empty] | POWER SUPPLY | [9 empty] | OTHER ITEMS | [5 empty] | FEEDERS
CIRCUIT | Number | MAGNET | Beamline | MAGNET | # | MAG. | MAG. |  | Cable Type | # of cables 1 way | R/kFt | L 1-way | Cable RES. | Cable Costs |  |  |  | Total Circuit Res. | Peak Current | Min. Current | dI/dT | Peak VOLT. | RMS CURR. | Peak Power |  | PS Location | PS TYPE | Max. Volt | Max. Curr. | PS Rating | Losses |  | Power Supply Costs |  |  |  | PS Installation Costs | [5 empty] | High Regulation | Quench Protection |  |  |  |  | AVE PWR | kVA | Amps
NAME | of Circuits | TYPE | Location & Distance along beamline (ft) | MODEL | MAGs | IND. | RES. |  |  |  | ohms | (ft) | ohms | M&S ($k) | Install ($k) | Tot. Cir ($k) |  | ohms | (amps) | (amps) | (A/s) | (volts) | (amps) | (kW) |  |  | SM or SCR | (volts) | (amps) | (kW) | (kW) | # | M&S ($k) | Tech. Labor (hrs) | Eng. Labor (hrs) |  | M&S ($k) | Tech. Labor (hrs) | Eng. Labor (hrs) | Elect. Labor (hrs) |  |  | M&S ($k) | M&S ($k) | Tech. Labor (hrs) | Eng. Labor (hrs) | SM V% | SM I % | (kW) | kVA | I
CritDev1 | 1 |  | BTL |  | 1 | 0.00454 | 0.026 |  | 500 | 2 | 0.026 | 335 | 0.00871 | 9.648 | 4.8374 | 14.4854 |  | 0.03471 | 500 | 500 | 0 | 17.355 | 500 | 8.6775 |  | Linac | SM | 30 | 668 | 20.04 | 1.5 | 1 | 16.6769 | 148 | 28 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 57.85 | 74.8503 | 10.1775 | 11.3083 | 13.6179
CritDev2 | 1 |  | BTL |  | 1 | 0.00454 | 0.026 |  | 500 | 2 | 0.026 | 354 | 0.009204 | 10.1952 | 5.1118 | 15.307 |  | 0.035204 | 500 | 500 | 0 | 17.602 | 500 | 8.801 |  | LInac | SM | 30 | 668 | 20.04 | 1.5 | 1 | 16.6769 | 148 | 28 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 58.6733 | 74.8503 | 10.301 | 11.4456 | 13.7832
Dipole_String | 1 |  | BTL |  | 30 | 0.00454 | 0.026 |  | 500 | 2 | 0.026 | 1468 | 0.038168 | 42.2784 | 21.1979 | 63.4763 |  | 0.81817 | 500 | 500 | 0 | 409.084 | 500 | 204.542 |  | F3 | SCR | 0 | 0 | 0 | 0 | 1 | 5 | 28 | 12 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | #DIV/0! | #DIV/0! | 204.542 | #DIV/0! | #DIV/0!
Bstr_Injct | 2 |  | Booster |  | 1 | 0.00454 | 0.026 |  | 500 | 2 | 0.026 | 200 | 0.0052 | 5.76 | 2.888 | 8.648 |  | 0.0312 | 500 | 500 | 0 | 15.6 | 500 | 7.8 |  | Bstr | SM | 30 | 668 | 20.04 | 1.5 | 2 | 33.3538 | 209.3036 | 39.598 |  | 2 | 16 | 12 | 30 |  |  | 3.1 |  |  |  | 52 | 74.8503 | 9.3 | 10.3333 | 12.4438
Beam_Dump | 1 |  | Dump Line |  | 5 | 0.00454 | 0.026 |  | 500 | 2 | 0.026 | 567 | 0.014742 | 16.3296 | 8.1875 | 24.5171 |  | 0.14474 | 500 | 500 | 0 | 72.371 | 500 | 36.1855 |  | F3 | SM | 80 | 625 | 50 | 4 | 1 | 24.0624 | 148 | 28 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 90.4638 | 80 | 40.1855 | 44.6506 | 53.7699
C-Magnet | 1 |  | BTL at Booster |  | 1 | 7.1e-05 | 0.005 |  | 500 | 4 | 0.026 | 200 | 0.0026 | 11.52 | 5.776 | 17.296 |  | 0.0076 | 1350 | 1350 | 0 | 10.26 | 1350 | 13.851 |  | Bstr | SCR | 50 | 1500 | 75 | 6.75 | 1 | 53 | 28 | 12 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 20.52 | 90 | 20.601 | 100.3947 | 120.8992
3-Way Septum | 1 |  | Dump Split |  | 2 | 7.1e-05 | 0.005 |  | 500 | 4 | 0.026 | 375 | 0.004875 | 21.6 | 10.83 | 32.43 |  | 0.014875 | 1350 | 1350 | 0 | 20.0813 | 1350 | 27.1097 |  | F3 | SCR | 50 | 1500 | 75 | 6.75 | 1 | 53 | 28 | 12 |  | 1 | 8 | 6 | 15 |  |  | 1.55 |  |  |  | 40.1625 | 90 | 33.8597 | 84.3067 | 101.5254
[49 empty] | 0 | #DIV/0! | #DIV/0!
[49 empty] | 0 | #DIV/0! | #DIV/0!
[49 empty] | 0 | #DIV/0! | #DIV/0!
[49 empty] | 0 | #DIV/0! | #DIV/0!
# of Circuits | 8 | [12 empty] | 9.648 | 58.8286 | 176.1598 | [32 empty] | 328.9667 | #DIV/0! | #DIV/0!
[33 empty] | 2010 Cost | [9 empty] | 2010 Cost
[15 empty] | TOTAL CABLE COSTS ($k): | 176.1598 | [6 empty] | Total Peak Power: | 306.9667 | kW | [6 empty] | TOTAL PS COSTS, M&S ($k): | 211.77 | [8 empty] | REGULATION INCREASE, M&S ($k): | 12.4
[34 empty] | Tech | Eng | [13 empty] | TOTAL M&S: | 408.3298 | 2010 $$
[5 empty] | NOTES: | [27 empty] | Total PS Labor (hrs): | 737.3036 | 159.598 | [13 empty] | TOTAL LABOR: | Tech | Eng. | Elect.
|  |  |  | * | Costs do not include cable tray in buildings, tunnels, cost of penetrations or load cable installation. | [27 empty] | (man-months): | 4.6081 | 0.99749 | [8 empty] | TOTAL QUENCH PROTECTION, M&S ($k): | 0 |  |  |  | MAN-HOURS | 801.3036 | 207.598 | 120
|  |  |  | * | M&S COSTS BASED ON 2018 | [30 empty] | Total PS Installation Costs, M&S ($k): | 8 | [10 empty] | TOTAL M&S |  | 473.6626
[38 empty] | Tech | Eng. | Elect. |  |  |  |  | Tech | Eng. |  | 2018 $$
|  |  |  | * | M&S savings based on number of units were not applied to "Power Supply Costs" or "High Regulation" - this is our experience | [31 empty] | Total PS Installation Labor (hrs): | 64 | 48 | 120 |  |  |  | Quench Prot. Labor (hrs): | 0 | 0
[37 empty] | (man-months): | 0.4 | 0.3 | 0.75 |  |  |  | (man-months): | 0 | 0
|  |  | 4-Quadrant Switch Mode PS Costs | [6 empty] | BASIC POWER SUPPLY COSTS | [6 empty] | For a single Power System, Rack and Filter | [8 empty] | For a Single power supply +/- 300 ppm regulation: | [8 empty] | For a Single power supply +/- 100 ppm regulation:
|  |  | M&S COSTS | $k | kW |  |  | SM POWER SUPPLY QUOTES | [8 empty] | 480 VAC Contrls | 1.3 | 1 | 1.3 | 2018 |  |  |  |  | LEM (1 kamp) | 0.3 | 1 | 0.3 | 2018 | [6 empty] | DCCT (1kamp) | 1.6 | 1 | 1.6 | 2018
|  |  | Ferm-built 65amp/150volt | [5 empty] | Manufacturer | Volts | Amps | Power | Cost | $/watt |  |  | Inductors | 0 | 0 | 0 | Eng Estimate |  |  |  |  | DAC | 0.2 | 1 | 0.2 | 2018 | [6 empty] | DAC | 0.2 | 1 | 0.2 | 2018
|  |  | 10kW | 4 | 10 | [6 empty] | (kW) | $k |  |  |  | Caps and Res. | 0 | 0 | 0 | Eng Estimate |  |  |  |  | DAC Card | 0.4 | 1 | 0.4 | 2018 | [6 empty] | DAC Card | 0.5 | 1 | 0.5 | 2018
|  |  | Raw power Supply | 5 | 22 |  |  |  | Magna-Power | 20 | 1000 | 20 | 11.8 | 0.59 |  |  |  |  | Subtotal: |  | 1.3 | ($k) |  |  |  | PC104 | 1 | 1 | 1 | 2018 | [6 empty] | PC104 | 1 | 1 | 1 | 2018
[9 empty] | Magna-Power | 32 | 750 | 24 | 14 | 0.58333 | [11 empty] | PLC | 1.4 | 1 | 1.4 | 2018 | [6 empty] | PLC | 1.4 | 1 | 1.4 | 2018
|  |  | LABOR | Tech |  |  |  |  | Magna-Power | 40 | 625 | 25 | 14 | 0.56 |  |  | Electrician | 1.2 | 1 | 1.2 | 15 | m-hrs |  |  |  | Reg. Chassis | 0.5 | 1 | 0.5 | 2018 | [6 empty] | Reg. Chassis | 0.5 | 1 | 0.5 | 2018
|  |  | SM Units | 3 | hrs |  |  |  | Magna-Power | 40 | 750 | 30 | 16.4 | 0.54667 |  |  | Power supply | 14 | 1 | 14 | 2018 |  |  |  |  | PS Int. Chassis | 0.5 | 1 | 0.5 | 2018 | [6 empty] | PS Int. Chassis | 0.5 | 1 | 0.5 | 2018
|  |  | Raw PSs and Rack | 50 | hrs |  |  |  | Sorenson (SG) | 40 | 375 | 15 | 9.3 | 0.62 |  |  | Rack | 2.5 | 1 | 2.5 | 2018 |  |  |  |  | LVPSs | 0.15 | 3 | 0.45 | 2018 | [6 empty] | LVPSs | 0.15 | 4 | 0.6 | 2018
|  |  |  | Eng |  |  |  |  | Lambda (GEN) | 40 | 250 | 10 | 5.8 | 0.58 |  |  |  |  | TOTAL: | 19 | ($k) |  |  |  |  | Back Plane | 0.2 | 1 | 0.2 | Engineering Estimate | [6 empty] | Back Plane | 0.2 | 1 | 0.2 | Engineering Estimate
|  |  | SM Units | 3 | hrs |  |  |  |  | Not used |  | See Calc Tab
|  |  | Design, layout, Raw PS | 20 | hrs |  | PHASE CONTROLLED (SCR) POWER SUPPLY COSTS | [11 empty] | LABOR | Tech | Eng | [6 empty] | Total: | 4.95 | ($k) | [8 empty] | Total (M&S): | 6.5 | ($k)
[9 empty] | Manufacturer: | votls | Amps | Power | Cost | $/watt |  |  |  |  | Assembly: | 1.5 | 0.2 | man-weeks
[12 empty] | (kw) | $k | [5 empty] | Testing: | 0.2 | 0.1 | man-weeks | [6 empty] | LABOR | Tech | Eng | [7 empty] | LABOR | Tech | Eng
[9 empty] | Spang: | 75 | 1000 | 75 | 48 | 0.64 | [14 empty] | Assembly: | 1.5 | 0.2 | man-weeks | [6 empty] | Assembly: | 1.5 | 0.2 | man-weeks
[9 empty] | 2018 | 150 | 500 | 75 | 48 | 0.64 | [14 empty] | Testing: | 0.5 | 0.2 | man-weeks | [6 empty] | Testing: | 0.5 | 0.2 | man-weeks
[29 empty] | Installation | 0.2 | 0.15 | man-weeks | [6 empty] | Installation | 0.2 | 0.2 | man-weeks
[10 empty] | V/I Regulator : | 5 | $k ea | 2018
(Fermi designed and built)
Note on N4: From the 2013 NEC Cost book via Ryan Crawford
Note on AD52: This supply is at the 80% limit

## $ per W Calc
Lambda Web Prices 5-21-19
Power(kW) | Price(k$) | $/kW | Calculation(k$)
0.75 | 1.604 | 2.1387 | 1.6181
1.5 | 1.915 | 1.2767 | 2.3633
2.4 | 2.902 | 1.2092 | 3.0738
3.3 | 3.698 | 1.1206 | 3.6807
5 | 4.612 | 0.9224 | 4.6659
10 | 6.618 | 0.6618 | 6.9585
15 | 8.873 | 0.59153 | 8.8066
Calculation Equation
(1.740.8*X^0.5823)+150