## Slide 1: Primary Beamline Radio-Activated Water (RAW) Peliminary Design Review
Horns A, B, & C RAW Systems
Karlton E. Williams, II
February 19, 2020

## Slide 2: RAW System - Preliminary Design Review Target Hall Layout For HORN RAW Systems
BEAM
Target Hall RAW Room
To Horn A
To Horn B
To Horn C
Horn C RAW
Horn B RAW
Horn A RAW
Target Chase
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
2

## Slide 3: RAW System - Preliminary Design Review Horns A, B, & C - General
Horns require many flow paths for cooling
4 manifolds each to feed spray nozzles
1 line each for hangers
Those 5 lines drain to sump tanks below horns, and are pumped back to expansion tanks via ejector pumps
1 line each for cooling modules, returns to expansion tank
1 line each for motive flow supply to ejector pumps
Plus one line for filtration
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
3

## Slide 4: RAW System - Preliminary Design Review Position Of Horns In Chase
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
4

## Slide 5: RAW System - Preliminary Design Review Horn A Close-Up
Main water manifold flex lines.
Hanger cooling line routing.
Module & SLB spacing confirmation.
Slide used courtesy Cory Crowley, Mike Campbell
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
5

## Slide 6: Main Manifold Flex lines
Slide used courtesy Cory Crowley, Mike Campbell
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
6
MANIFOLDS
NOZZLES

## Slide 7: Hanger Cooling Union Line
Slide used courtesy Cory Crowley, Mike Campbell
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
7

## Slide 8: RAW System - Preliminary Design Review
Interior view of horn with spray nozzle patterns
Slide used courtesy Cory Crowley, Mike Campbell
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
8

## Slide 9: RAW System - Preliminary Design Review Horns A, B, & C – Heat Loads
LBNF Horn RAW Systems – Heat Loads (units kW) |  |  |  |  |  | 
 | Horn A |  | Horn B |  | Horn C | 
Heat Source | 1.2MW | 2.4MW 1 | 1.2MW 1 | 2.4MW 1 | 1.2MW 1 | 2.4MW 1
Manifold A | 8 | 16 | 7 | 14 | 4.5 | 9
Manifold B | 8 | 16 | 7 | 14 | 4.5 | 9
Manifold C | 8 | 16 | 7 | 14 | 4.5 | 9
Manifold D | 15 | 30 | 12.5 | 25 | 8.5 | 17
Modules | 3.3 | 6.6 | 3 | 6 | 6 | 12
Hangers | 1.5 | 3 | 1 | 2 | 1 | 2
Ejector Pump Supply | n/a | n/a | n/a | n/a | n/a | n/a
Filter/DI Loop | n/a | n/a | n/a | n/a | n/a | n/a
Recirc Pump | 18.6 | 29.8 | 37.2 | 37.2 | 29.8 | 29.8
SYSTEM TOTAL | 62.4 | 117 | 74.7 | 91.2 | 58.8 | 87.8
Notes:
1 – The horn & module heat load numbers for all three horns are based on actual EDEP analysis for 1.2MW. All 2.4MW numbers are 1.2MW X 2. They are fairly accurate and not actually scaled off of Horn A.
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
9

## Slide 10: RAW System - Preliminary Design Review Horns A, B, & C - Flows
LBNF Horn RAW Systems – Required Flows (units gpm) |  |  |  |  |  | 
 | Horn A |  | Horn B 2 |  | Horn C 2 | 
Flow Source | 1.2MW | 2.4MW1 | 1.2MW1 | 2.4MW1 | 1.2MW1 | 2.4MW1
Manifold A | 8.1 2 | 16.2 | 24.3 | 24.3 | 16.2 | 16.2
Manifold B | 8.1 2 | 16.2 | 24.3 | 24.3 | 16.2 | 16.2
Manifold C | 8.1 2 | 16.2 | 24.3 | 24.3 | 16.2 | 16.2
Manifold D | 15.1 2, 4 | 30.2 | 45.3 | 45.3 | 30.2 | 30.2
Modules | 34 | 34 | 34 | 34 | 34 | 34
Hangers | 3 2 | 3 | 3 | 3 | 3 | 3
Ejector Pump Supply | 52 | 100 | 142 | 142 | 100 | 100
Filter/DI Loop | 10 | 10 | 20 | 20 | 20 | 20
SYSTEM TOTAL (Recirc Pump) | 140 | 242 | 314 | 314 | 242 | 242
Notes:
1 – Based on scaling of Horn A at 1.2 MW
2 – Values add to produce total flow required by ejector pump suction flow
3 – Horns B and C, system size governed by horn spray flow required, not heat removal
4 – Flow includes Target Mount @ 2.9 gpm
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
10

## Slide 11: RAW System - Preliminary Design Review Horns A, B, & C - Design Maturity
Horns on a later maturity schedule than most TH/AH components
EDEP modeling done for all 3 horns at 1.2MW
Work on Horn A prototype in progress
Horns B and C to follow later
Horn design for 2.4MW operation may be different than 1.2MW
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
11

## Slide 12: RAW System - Preliminary Design Review Horns A, B, & C – RAW System Design
Horn RAW System design strategy:
Preliminary design of Horn A for 1.2MW
  Includes EDEP, spray nozzle flows, as required of RAW system
  Includes hangers, modules, ejector pump
Complete prototyping of ejector pump
EDEP for cooling requirements completed for Horns B & C
Heat loads are doubled for 2.4MW operation
Flows are scaled as Horn B = 3 x Horn A, Horn C = 2 x Horn A
Use this model for basis of Horns B and C design
Prototype ejector pump work will include requirements for all 3
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
12

## Slide 13
Heat loads are similar between the 3 horns
  Original estimates had Horns B & C greater than Horn A
  Horn B is about 90% of horn A, Horn C is about 65% of Horn A
  The hangers and modules vary some as well
  Driving item is flow required for even spray within the horn interiors
  Significant contributor to hear load is recirculation pump
Horn A, heat load is dominant design requirement
  By value engineering, may be outfitted with smaller recirc pump and heat exchanger for 1.2MW beam
Horns B & C, flows for inner horn spray wands are dominant design requirement
  Require same system for either 1.2MW or 2.4MW beam power
RAW System - Preliminary Design Review Horns A, B, & C
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
13

## Slide 14: RAW System - Preliminary Design Review Horns A, B, & C
To evacuate Horn Water Tanks, Ejector (jet) Pump sizing becomes key
Motive flows required for Ejector Pumps are approximately 1.5 times that as being removed from the Horn Water Tanks
  Water from internal spray wands collects in water tanks (troughs) below the horns
  Must then be suctioned out by ejector pumps (AKA eductor or jet pumps)
  System total flow = spray wand flow + motive flow + filtration
    Approx. total system flows = 2.5 to 3 times Horn spray wand flows
  Because of high pressure and flow requirements of the motive flow stream, recirculation pumps are much larger than required for simple supplying the horn cooling flows
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
14

## Slide 15
Why ejector pumps?
  No moving parts to wear, all SS
  No electrics to burn out
  Ability to be mounted above modules for easy access & maintenance
Prototyping
  Will test single pump, and dual pumps in parallel
  Will test accurate mock-up of suction tube and fittings for realistic assessment of losses in actual circumstances
  May affect pump chosen
  May affect current suction line design
RAW System - Preliminary Design Review Horns A, B, & C
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
15

## Slide 16
Suction lifts required are 17’ for Horn A, 18.5’ for Horns B, & C
  Add approx. 5’ for friction head loss
  Sum of lift losses greatly affects ejector performance
  Discharge back pressure = 11 psid = 25’
  Require higher pressures of motive flow to acquire lift, and to overcome backpressure to return to RAW reservoir
    Motive supply pressure to ejector of 100psig or greater
    Ejector pumps will be below the hatch covers, above the modules
    Requires refinement of engineering, and prototype installation testing, which is in planning stages by J. Chikelu
RAW System - Preliminary Design Review Horns A, B, & C
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
16

## Slide 17
To increase suction lift head, must increase motive (input) pressure and flow, and/or decrease discharge backpressure
To increase suction flow, must increase motive pressure and flow, decrease backpressure, and/or reduce required suction lift head
At our needs, motive flow required >> suction fluid flow desired
Image Credit: Pentair Penberthy Jet Pumps
Suction Lift Required: Horn A = 17 ft = -7.4 psig
Horn B = 18.5 ft = -8.0 psig
Horn C = 18.5 ft = -8.0 psig
Ejector Pump Basics:
Motive Fluid In
Discharge Out
Suction Fluid In From Horn Sump
= Motive + Suction Fluids To RAW Skid
From RAW Skid
RAW System - Preliminary Design Review Horns A, B, & C
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
17

## Slide 18
Complex system to model
Manifolds - modeled each manifold with spray nozzles as a single entity with a system curve
Suction line - modeled multiple sections & sizes of suction line, from horn capture tank to ejector, as a single entity with a system curve
Discharge line - verified discharge line from ejector to expansion tank with a model
Substituted manifold and suction curves into Fathom system model
RAW System - Preliminary Design Review Horns A, B, & C – AFT Fathom Modeling
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
18

## Slide 19
Must “fool” the model at times
  AFT Fathom models a symbolic ejector with only a suction and a discharge line, not all 3 lines
  Supply to motive line is to pressure node
  Flow from nozzles cannot be tied directly to horn capture tank
  Make links between the above entities by setting up “design alerts” if conditions between junctions or pipes are not met, then iterate until alerts are met
RAW System - Preliminary Design Review Horns A, B, & C – AFT Fathom Modeling (cont.)
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
19

## Slide 20
Files at Dune DocDB 17873 https://docs.dunescience.org/cgi-bin/private/AddFiles
Horn A main 2-18-20.pdf
Horn A manifolds A-B-C 2-18-20.pdf
Horn A manifold D 2-18-20.pdf
Horn A suction line 2-18-20.pdf
Horn A discharge line 2-18-20.pdf
RAW System - Preliminary Design Review Horns A, B, & C – AFT Fathom Modeling (cont.)
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
20

## Slide 21
RAW System - Preliminary Design Review Horns A, B, & C – AFT Fathom Modeling (cont.)
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
21
Simplified Ejector Model
Manifolds
Hangers
Modules
Expansion Tank
Recirc Pumps

## Slide 22
RAW System - Preliminary Design Review Horns A, B, & C – AFT Fathom Modeling (cont.)
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
22
Manifolds A, B, C

## Slide 23
RAW System - Preliminary Design Review Horns A, B, & C – AFT Fathom Modeling (cont.)
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
23
Manifold D

## Slide 24
RAW System - Preliminary Design Review Horns A, B, & C – AFT Fathom Modeling (cont.)
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
24
Suction Line
Discharge Line

## Slide 25
Designed for all pipes to fit into envelope 18”h x 18”w
  4 manifold lines
  2 module lines
  1 hangers line
  1 ejector supply line
  1 ejector return line
  2 argon circulation gas lines
  1 spare line
Fully welded SS, from RAW system in RAW Room, through penetration to Target Hall, along aisle and thru penetration at battlement into Target Chase
Removable sections inside Chase flanged at battlement
All isolation valves, flow controls, at system in RAW Room
RAW System - Preliminary Design Review Horns A, B, & C - Piping Runs
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
25

## Slide 26: RAW System - Preliminary Design Review

## Slide 27: RAW System - Preliminary Design Review Hermetic Seal At Battlement Penetration

## Slide 28: RAW System - Preliminary Design Review
Target Hall RAW Room
TARGET HALL COMPLEX
Target Chase
Piping Path Envelope

## Slide 29: RAW System - Preliminary Design Review Horns A, B, & C
2/20/2020
Karl Williams | Horns A, B, & C RAW Systems
29
Questions?