## Slide 1: Primary Beamline Target Shield Pile Cooling Panel RAW System Preliminary Design Review
Technical Design Aspects
Raina Wang
February 19, 2020

## Slide 2: Purpose and Scope
Preliminary design of the Target Shield Pile (TSP) Cooling Panel radioactive water (RAW) system to cool the inner layers of steel shielding of the target chase in Target Hall for 2.4MW beamline of LBNF project.
  To supply and return cooling water for:
    36 cooling panels, 18 each side of the target chase
    8 small panels - attached to the bottom of some t-blocks

## Slide 3: Purpose and Scope – Cont.
A stand along skid: equipment, pipes, valves, fittings, and field installed instruments
Piping and piping components between the skid and the nozzles of 44 panels
First valve between:
  LBNF TH Exchange System and
  Intermediate Water System, which covers the pipes
Mechanical techniques for mitigating radiation risks
All other EHS related radiation dose rate evaluations and control are excluded from this system
  They are the work scope of ESH or Radiation Physicist Department

## Slide 4: Purpose and Scope – Cont.

## Slide 5: Design Standards and Codes
ASME B31.3 Code for Normal Fluid Service
ASME BPVC Section IX for Welding Process Specifications (WPS’s) and welders & pipefitters' Personal Weld Qualifications
Both piping and vessels will adhere to FESHM Chapter 5031, as well as the Fermilab Engineering Manual
Numi/Nova systems’ general operational feedbacks for improvement

## Slide 6: Design Requirements
Safe, Reliable, and Economic
Convenient for operation and maintenance
Meet water quality and capacity of operational requirements for:
  1.2MW beamline – first phase
  2.4 MW beamline – 2nd phase
Design depth – sufficient for cost estimating for Project Budget

## Slide 7: Design Requirements – Process By Matt Slabaugh and Joseph Angelo

## Slide 8: Design Capacity – 450 GPM

## Slide 9: Equipment Selection and Sizing - Heat Exchanger
Capacity: 900 KW, actual 950KW
Type: Tranter Superchanger plate and frame unit
- a welded unit
- eliminate leaking
Material: SS
CS shell and cover - optional
ASME code compliance
Design condition: 150Psig @ 200oF
MAWP: ≥200 Psig
MMDT: -20 deg. F
Hot side: Temperature – ΔT = 15deg.
Tin = 85 deg. F Tout = 100 deg. F
Flow rate – 435 GPM
Cold side: temperature - ΔT = 12 deg.
Tin = 65 deg. F Tout = 77 deg. F
Flow rate – 490 GPM

## Slide 10: Equipment Selection and Sizing – Heat Exchanger

## Slide 11: Equipment Selection and Sizing – Pumps, Piping, Control Valves
Sizing method: Hydraulic simulation
Sizing technology: AFT Fathom software, version 9
Multiple operation modes simulated:
  Design condition (2.4MW beamline): 450 GPM
  1.2MW beamline condition: 147 GPM
Results:
  Pump: 450 GPM @ 143 ft TDH
  Pipe header: 5” NPD and branch head 4” NPD
  Control valve: 3”

## Slide 12: Equipment Selection and Sizing – Cont. - AFT Fathom Simulation Results

## Slide 13: Equipment Selection and Sizing – Cont. - AFT Fathom Simulation Results

## Slide 14: Equipment Selection and Sizing – Cont.: - AFT Fathom Simulation Results

## Slide 15: Equipment Selection and Sizing – Cont. - Pump Selected, Sized
Two Centrifugal Pumps: one op / one standby
Type: Canned motor centrifugal pumps – Sealless
Capacity Index:
  450 GPM @143 ft TDH, meet max. flow requirements of 2.4MW
  Min. flow: 110 GPM
  Min. flow meet 1.2 MW beamline requirements: 147 GPM
  Cut off flow: 100 GPM
  Shut off head: 175 ft
Variable speed control: Benefit and radiation degradation
- based on Numi operation experience

## Slide 16: Equipment Selection and Sizing – Cont. - Pump Selected, Sized

## Slide 17: Equipment Selection and Sizing – Cont. - Detailed Equipment List and Spec

## Slide 18: Process Flow – Piping & Instrumentation Diagram

## Slide 19: Water Quality Control
Initial fill: LCW – from TH RAW Exchange System
Impurity concentration increases with time
Control:
  Argon blanketing in storage tank
  Periodic burping predetermined amount of RAW
  Filtration:
    DI loop: 2 stage filtration in series: one 20µm / one 5µm
        Impurity particle size less than: 5µm
        Extra filter guard in case DI problem: <=20µm
        Fermi conventional DI bottle – 4 in one Cask
  Maintaining Water resistivity: 4 – 8 MΩ×cm

## Slide 20: ESH – Radiation Risk Control
Risks:
  Initial LCW - to be radioactiviated after short running – becoming RAW
  The prompt radiation dose rates from the RAW skid – high!
  Short-lived radionuclides, large concentrations of the tritium will build up in the systems
Mechanical Controls:
To prevent RAW from intermixing with the environment, the cold side cooling water of the heat exchanger is supplied by and discharged to an adjacent Intermediate Water System
Clean in place containment - for RAW leakage, spill and tritium capture
- preventing soil and surface water contamination
Remotely controlled drainage and top up with fresh water - used to keep the tritium concentrations at manageable levels
Wastewater will be disposed of as low-level radioactive waste after cooling-down or decayed
Radiation hardened materials – equipment, piping components
Electronic devices: P, T, Q, L transmitters - installed further away from high radiation area to prevent radiation degradation

## Slide 21: Equipment and Piping Layout - Plan View
RAW supply and return head, 5” NPD

## Slide 22: Equipment and Piping Layout - 3D Top View
TSP Cooling Panel RAW Skid
RAW supply and return head, 5” NPD
Target Chase

## Slide 23: Equipment and Piping Layout - 3D View
Target Chase
TSP Cooling Panel RAW Skid
RAW supply and return head, 5” NPD

## Slide 24
Questions?
Thank You!
By Raina Wang
Mechanical Beamline Engineer
Feb. 19, 2020