## Slide 1: Primary Beamline Target Hall RAW Exchange System Preliminary Design Review
Technical Design Aspects
Raina Wang
February 19, 2020

## Slide 2: Purpose and Scope
Preliminary design of the Target Hall (TH) RAW Exchange System for the 2.4MW beamline radioactive cooling water (RAW) systems of LBNF project
Includes four independent functional sections:
  Make-up supply or Fill of low conductivity water (LCW) to all the five RAW and Intermediate Water Systems in the same RAW room of the Target Hall Complex :
      Target RAW system – Target Mount, Hanger, Helium heat exchanger, and Baffle
      Horn A RAW system
      Horn B RAW system
      Horn C RAW system
      Target Shield Pile Cooling Panel RAW system
      Intermediate Water System
  Burping or periodically removing predetermined quantity of RAW from the 5 RAW systems during operation to reduce the contamination concentration of the RAW and thus maintain required cooling water quality.
  Draining all 6 or any single RAW cooling system and intermediate water system completely during repair and maintenance modes
  Transferring all the drained RAW or wastewater into radiation safe drums located outside of Target Hall for radioactive waste safe disposal – hauling offsite

## Slide 3: Purpose and Scope – Cont.
A stand along area in the RAW room: equipment, pipes, valves, fittings, and field installed instruments
Piping and piping components between 6 pumps in this system and the 6 RAW skids and Intermediate Water system
  except their first valve if there is one.
Mechanical techniques for mitigating radiation risks
All other EHS related radiation dose rate evaluations and control are excluded from this system
  They are the work scope of ESH or Radiation Physicist Department

## Slide 4: Purpose and Scope – Cont.
Horn A/B/C RAW
Target RAW System

## Slide 5: Design Standards and Codes
In addition to comply with the following industrial and Fermilab standards and codes, the system design, particularly the system’s operation modes, capacity, and valve regulating & controls, is mainly based on Numi/Nova systems’ operational experience, lessons learned, and the latest feedback in operational input and upgrades.
ASME B31.3 Code for Normal Fluid Service
ASME BPVC Section IX for Welding Process Specifications (WPS’s) and welders & pipefitters' Personal Weld Qualifications
Both piping and vessels will adhere to FESHM Chapter 5031, as well as the Fermilab Engineering Manual
ASTM-D-1998-15, Standard Specification for Polyethylene Upright Storage Tanks

## Slide 6: Design Requirements - General
Safe, Reliable, and Economic
Convenient for maintenance
Meet water quality and capacity of operational requirements for:
  1.2MW beamline – first phase
  2.4 MW beamline – 2nd phase as Designed phase
Design depth – sufficient for cost estimating for Project Budget

## Slide 7: Design Capacity - depends on operation modes
Operation Modes
  Every functional section is required to be in operating one skid unit each time per Numi operation procedure
  meaning that no two systems will be running simultaneously,
Capacity sizing: Thus, the equipment and piping header of every functional section is sized at the same flow rate of every single unit’s flow rate
  Detailed design capacity and pressure of all sections are summarized in Table -1

## Slide 8: Design Capacity

## Slide 9: Equipment Selection and Sizing – Pumps, Piping, Pressure Regulators
Sizing method: Hydraulic simulation
Sizing technology: AFT Fathom software, version 9
Multiple operation modes simulated:
  LCW filling pump sizing
  RAW skid drain Inline pump sizing
  RAW transfer pump sizing
  5 RAW burping pressure regulator sizing
    Burping pressure: 60 to 120 psig
    Destination pressure at RAW holding tank: Atm. P

## Slide 10: Equipment Selection and Sizing – AFT Fathom Simulation Results – LCW pumps

## Slide 11: Equipment Selection and Sizing – AFT Fathom Simulation Results – Inline Pump Selected
self-priming pump

## Slide 12: Equipment Selection and Sizing – AFT Fathom Simulation Results – Transfer Pumps Selected

## Slide 13: Equipment Selection and Sizing – AFT Fathom Simulation Results – Intermediate Water System Drain Pump Selected

## Slide 14: Equipment Selection and Sizing – AFT Fathom Simulation Results – Horn A RAW Burping Regulator sizing
RAW burping simulations of other 4 RAW skids is similar to Horn A’s
Results of 5 operation modes simulated:
- Initial burping @ 80 and 120 psig – 2 Pressure regulators
- Different setting pressure needed.

## Slide 15: Equipment Selection and Sizing – Cont. - Detailed Equipment List and Spec

## Slide 16: Process Flow – Piping & Instrumentation Diagram

## Slide 17: Water Quality Control
The initial water supply for filling is pretreated city water from Fermilab LBNF Target Hall Power Supply Room (see P&ID drawing F10127809).
It is then filtered by two stage cartridge filters:
  one 20µm
  one 5µm ultrafine
  Control ultimate impurity particle size below 5um for all the downstream users
One Fermilab conventional DI bottles is used for controlling water resistivity within a range of 4 to 8 MΩ × cm.
Argon gas blanketing for the storage tank - To preventing contamination gas such as CO2 from entering the system

## Slide 18: ESH – Radiation Risk Control
Risks:
  Initial LCW - to be radioactiviated after short running of those RAW cooling skids – becoming RAW
The following mechanical techniques are used for mitigating RAW radiation risks and increase system reliability:
  Radiation hardened materials are selected for all equipment and piping components
  Clean in place containment tanks and warning alarms are designed to prevent spills and contamination of the soil and surface waters
  Remotely controlled drainage and top up with fresh water will be used to keep the tritium concentrations at manageable levels. Wastewater will be disposed of as low-level radioactive waste after cooling-down
  Electronic devices such as fluid measurement transmitters will be installed further away from the high radiation area to prevent radiation degradation

## Slide 19: Equipment and Piping Layout - 3D Top View
Horn A/B/C RAW
Target RAW System

## Slide 20: Equipment and Piping Layout - 3D View, area detail
Inline pump - burping
RAW holding tank, 1200 Gal
Poly material & transfer pumps
LCW storage tank 200 Gal & pumps
DI bottle & Filter
Intermediate water system drain pump

## Slide 21: Equipment and Piping Layout - 3D View

## Slide 22
Questions?
Thank You!
By Raina Wang
Mechanical Beamline Engineer
Feb. 19, 2020

## Slide 23: Equipment Selection and Sizing – 1200 Gal Holding Tank

## Slide 24: Equipment Selection and Sizing – LCW Pumps Selected

## Slide 25: Field Instruments and Valve List & Spec _ Page 1 of 3

## Slide 26: Field Instruments and Valve List & Spec _ Page 2 of 3

## Slide 27: Field Instruments and Valve List & Spec _ Page 1 of 3

## Slide 28: Piping and Fitting Estimating

## Slide 29: Design Requirements – Process Data Provided by operation engineer - Abhishek Deshpande

## Slide 30: Design Requirements – Process Data Provided by operation engineer - Abhishek Deshpande, verified by Karlton E Williams II

## Slide 31: Design Requirements – NProcess Data Provided by operation engineer - Abhishek Deshpande, verified by Karlton E Williams II