## ChangeLog
Date | Comments | Verified by
2019-04-05 | HPRF revision - heat load | J.Steimel
2019-05-23 | VE - LB650 4 cav implementation | F.G.Garcia in consultation with L3Ms (BI, LLRF, HPRF)
2019-05-28 | Add F3 Building as a location for some BTL equipment (this includes B.Hanna changes on rack power needs and rack# for the BTL system) | D. Morris
2019-05-31 | Add RF Separator Requirements at the Gallery | E. Pozdeyev, S. Dixon, C. Baffes, P. Derwent/E. Harms, F.G. Garcia (RF sep. requirements)
2019-06-12 | Updated PUB LCW and General Data Acquisition Rittal Rack dimensions Clarified Joe Ozelis's notes on the flow rate of exhausted air from the cryomodule couplers | J. Hunt, E. Huedem, R. Crawford, D. Newhart, and F.G. Garcia
2019-07-12 | Updated Heat Load to Air and Power requirements of amplifier to incorporate the 44% Eff. measured at RRCAT (JS) | J. Hunt, R. Crawford, D. Newhart, and F.G. Garcia, J. Steimel
2019-08-28 | Number of Racks - align with R. Crawfor Rack Layout as 08/28/2019 | R. Crawford
2019-09-06 | Release after Jamboree August 29, 2019 | Official Release of RDS - Jamboree Aug 2019

## Sheet1
Identifier | WBS Level 2 | WBS ID | WBS Name | Building | Space Designation Location | Sub-System | User Defined Sub-System | Component | Description | Identifier - To Be Deleted | Quantity | Level of Design | Source of Requirements | Uncertainty Multiplier | Space Type | Length (in) | Width (in) | Height (in) | Weight (lbs) | Floor Flatness | Vibration | Finishes | Heating (F) | Cooling (F) | Humidity (%) | Pressurization Requirement | ODH (air changes/hr) | Any Special Ventilation (CFM) | Cooling Type | Heat Load (KW) | Total Heat Load (KW) | Heat Load to Air from Cables (KW) | Supply Nominal (F) | Supply Max (F) | Stability (F) | ΔT (F) | Power Requirement | Volts | Amps | Volt-Amperes | Total KVA | Power Factor (%) | Total Power (KW) | UPS (kVA / time (min)) | Standby Power (kVA) | Breaker (A) | Line Filter? | Dedicated Disconnect? | Special LOTO Provisions? | Special Grounding Required? | Size | Front Access | Closed Sides | Rear | Access to Power or Signal Cable Tray? | Cable Type | Count | Load greater than 50 V/100 A | Xrays? | ESS (Electrical Safety System) | Please select type of comm. | Other Requirements or Comments
JO-008 | 121.02 | 121.02.04 | Elliptical | LT | LT-HB650 | HB650 Cryomodule |  | Couplers | 6 cavities x 4 CMs |  | 24 | Preliminary | Prototype-Testing | 0.25 | [14 empty] | Air, Compressed | 0.45833 | 11 |  | 70 | 75 | [5 empty] | 0 | 0 | 100 | 0 |  |  |  |  | No | No | No | [7 empty] | No | No | No | NA | Air flow = 33 SCFM per cryomodule (for 6 CMs use 198 cfm)
JO-006 | 121.02 | 121.02.04 | Elliptical | LT | LT-HB650 | HB650 Cryomodule |  | Cryomodule |  |  | 6 | Preliminary | Off the Shelf | 0.05 | Floor | 391 | 82 | 88 | 27700 |  | TBD | Sealed concrete | [8 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 |  |  |  |  | No | No | No | [7 empty] | No | Yes | No | NA

## Pivot Table
WBS Name | (All)
Building | (All)
Cooling Type | (All)
Space Designation Location | (All)
Sub-Systems and Components | Sum of Quantity | Sum of Total Heat Load (KW) | Sum of Total KVA | Sum of Total Power (KW)
4.5K Cold Box
Cold Box Station | 2 | 0 | 6.593 | 6.593
Absorber Assembly
MEBT | 1 | 20 | 0 | 0
Air Compressor
Compressed Air | 2 | 12 | 55.3702 | 55.3702
Allison Scanner
Ion Source | 4 | 2.4 | 0 | 0
Bottle Enclosure
Ion Source | 1 | 0 | 0 | 0
Bottles
Resistivity Control | 3 | 0 | 0 | 0
Bunching Cavities
MEBT | 4 | 6 | 0 | 0
Cabinets
Ion Source | 4 | 0.4 | 70.1108 | 70.1108
WFE | 1 | 0.5 | 1.8 | 1.8
Cables
Fast Dipole Switch | 8 | 0 | 0 | 0
Magnets, Dipole | 36 | 0 | 0 | 0
Magnets, Dipole Corrector | 56 | 0 | 0 | 0
Magnets, Regular Quadrupole | 32 | 0 | 0 | 0
Chopper
LEBT | 1 | 0.3 | 0 | 0
Circulators
HB650 | 36 | 0 | 0 | 0
HWR | 8 | 0 | 0 | 0
LB650 | 36 | 0 | 0 | 0
RFQ | 2 | 0 | 0 | 0
SSR1 | 16 | 0 | 0 | 0
SSR2 | 35 | 0 | 0 | 0
Cold Box Equipment
Cold Box Station | 4 | 15 | 73.7969 | 73.7969
Compressors
Warm Compressor Section | 3 | 127 | 590.2829 | 590.2829
Consoles, Fixed
Computers, Console | 13 | 0.68 | 6.24 | 6.24
Consoles, Mobile
Computers, Console | 10 | 0.6 | 4.8 | 4.8
Controller, Ion Pump
BTL/BAL | 57 | 5.7 | 0.82931 | 0.82931
HB650 | 6 | 0.6 | 0.087295 | 0.087295
HWR | 1 | 0.1 | 0.014549 | 0.014549
LB650 | 9 | 0.9 | 0.13094 | 0.13094
RFSeparator | 2 | 0.2 | 0.029098 | 0.029098
SSR1 | 2 | 0.2 | 0.029098 | 0.029098
SSR2 | 7 | 0.7 | 0.10184 | 0.10184
WFE | 9 | 0.9 | 0.13094 | 0.13094
Controller, Ion/Pirani Gauge
BTL/BAL | 10 | 1 | 0.6 | 0.6
HB650 | 12 | 1.2 | 0.72 | 0.72
HWR | 2 | 0.2 | 0.12 | 0.12
LB650 | 18 | 1.8 | 1.08 | 1.08
RFSeparator | 2 | 0.2 | 0.12 | 0.12
SSR1 | 4 | 0.4 | 0.24 | 0.24
SSR2 | 21 | 2.1 | 1.26 | 1.26
WFE | 17 | 1.7 | 1.02 | 1.02
Controller, Turbo Pump
BTL/BAL | 2 | 0 | 0.24 | 0.24
HB650 | 6 | 0 | 0.62354 | 0.62354
HWR | 1 | 0 | 0.10392 | 0.10392
LB650 | 9 | 0 | 0.93531 | 0.93531
RFSeparator | 0 | 0 | 0 | 0
SSR1 | 2 | 0 | 0.20785 | 0.20785
SSR2 | 7 | 0 | 0.72746 | 0.72746
WFE | 11 | 0 | 1.32 | 1.32
Couplers
HB650 Cryomodule | 24 | 11 | 0 | 0
HWR Cryomodule | 8 | 0.2 | 0 | 0
LB650 Cryomodule | 36 | 11.04 | 0 | 0
RFQ | 4 | 0.84 | 0 | 0
SSR1 Cryomodule | 16 | 0.816 | 0 | 0
SSR2 Cryomodule | 35 | 6.3 | 0 | 0
Cryomodule
HB650 Cryomodule | 6 | 0 | 0 | 0
HWR Cryomodule | 1 | 0 | 0 | 0
LB650 Cryomodule | 9 | 0 | 0 | 0
SSR1 Cryomodule | 2 | 0 | 0 | 0
SSR2 Cryomodule | 7 | 0 | 0 | 0
Dryer
Compressed Air | 2 | 0.1 | 1.564 | 1.564
Element/magnet
Magnets, Dipole Corrector | 16 | 0 | 0 | 0
Solenoids | 8 | 0 | 0 | 0
Entire Area
Network Room | 1 | 0 | 0 | 0
Warm Compressor Section | 1 | 200 | 0 | 0
Gauges, Ion
BTL/BAL | 12 | 1.2 | 0 | 0
HB650 | 16 | 1.6 | 0 | 0
HWR | 3 | 0.3 | 0 | 0
LB650 | 36 | 3.6 | 0 | 0
RFSeparator | 0 | 0 | 0 | 0
SSR1 | 8 | 0.8 | 0 | 0
SSR2 | 28 | 2.8 | 0 | 0
WFE | 17 | 1.7 | 0 | 0
Gauges, Pirani
BTL/BAL | 10 | 1 | 0 | 0
HB650 | 16 | 1.6 | 0 | 0
HWR | 3 | 0.3 | 0 | 0
LB650 | 36 | 3.6 | 0 | 0
RFSeparator | 0 | 0 | 0 | 0
SSR1 | 8 | 0.8 | 0 | 0
SSR2 | 28 | 2.8 | 0 | 0
Generator
Cold Box Station | 1 | 0 | 0 | 0
Heat Exchanger
LCW | 1 | 0 | 0 | 0
Interlock Box
Interlocks | 2 | 0 | 0.72 | 0.72
Ion Source
Ion Source | 2 | 24 | 0 | 0
Kickers
MEBT | 2 | 1 | 0 | 0
Laser Room
Laser Wire | 2 | 0 | 10.808 | 10.808
Magnets
Fast Dipole Switch | 1 | 0 | 0 | 0
LEBT | 1 | 0.05 | 0 | 0
Magnets, Dipole Corrector | 208 | 7.04 | 0 | 0
Magnets, Regular Quadrupole | 98 | 56.31 | 0 | 0
Solenoids | 29 | 0 | 0 | 0
NEG
WFE | 2 | 0.2 | 0 | 0
NEG Controller
WFE | 2 | 0 | 0 | 0
Panels
Ion Source | 2 | 0.1 | 6.24 | 6.24
Warm Compressor Section | 2 | 0 | 0 | 0
Power Amplifiers
HB650 | 36 | 3968.1818 | 7610.9937 | 6545.4545
HWR | 8 | 66.2836 | 141.4141 | 127.2727
LB650 | 36 | 1832.7273 | 3805.4968 | 3272.7273
RFQ | 2 | 300 | 299.2984 | 299.2984
RFSep- HPRF | 1 | 103.9909 | 206.6822 | 177.7467
SSR1 | 16 | 147.5345 | 282.8283 | 254.5455
SSR2 | 35 | 890.9091 | 1767.6768 | 1590.9091
Power Supplies
BTL/BAL | 3 | 0 | 1.5547 | 1.5547
LEBT | 2 | 0.1 | 3.6 | 3.6
Magnets, Dipole | 3 | 52 | 436.4768 | 392.8291
Magnets, Dipole Corrector | 168 | 0 | 0 | 0
Magnets, Regular Quadrupole | 40 | 0 | 0 | 0
MEBT | 4 | 0.4 | 7.2 | 7.2
RFQ | 1 | 0.05 | 1.8 | 1.8
RFSep-BLVac | 1 | 0 | 0.5404 | 0.5404
RFSep-Magnets, BLQuads | 8 | 4 | 66.5108 | 55.869
RFSep-Magnets, Lambertson | 3 | 1.5 | 24.9415 | 20.9509
RFSep-Magnets, Vert. Dip. | 2 | 1 | 16.6277 | 14.2998
RFSep-Spang | 5 | 60 | 519.6152 | 467.6537
Solenoids | 37 | 0 | 0 | 0
WFE | 1 | 0 | 0.10184 | 0.10184
Pump
LCW | 4 | 111 | 558.6903 | 558.6903
Pump, Ion
BTL/BAL | 57 | 5.7 | 0 | 0
HB650 | 4 | 0.4 | 0 | 0
HWR | 1 | 0.1 | 0 | 0
LB650 | 9 | 0.9 | 0 | 0
RFSeparator | 0 | 0 | 0 | 0
SSR1 | 2 | 0.2 | 0 | 0
SSR2 | 7 | 0.7 | 0 | 0
WFE | 9 | 0.9 | 0 | 0
Pump, Roughing
HB650 | 4 | 2 | 4.16 | 4.16
HWR | 1 | 0.5 | 1.04 | 1.04
LB650 | 9 | 4.5 | 9.36 | 9.36
RFSeparator | 0 | 0 | 0 | 0
SSR1 | 2 | 1 | 2.08 | 2.08
SSR2 | 7 | 3.5 | 7.28 | 7.28
Pump, Turbo
BTL/BAL | 2 | 1 | 0.96 | 0.96
HB650 | 4 | 2 | 1.92 | 1.92
HWR | 1 | 0.5 | 0.48 | 0.48
LB650 | 9 | 4.5 | 4.32 | 4.32
RFSeparator | 0 | 0 | 0 | 0
SSR1 | 2 | 1 | 0.96 | 0.96
SSR2 | 7 | 3.5 | 3.36 | 3.36
WFE | 11 | 5.5 | 5.28 | 5.28
Pumps
RAW Absorber | 1 | 75 | 4.1569 | 4.1569
Rack Mount
Interlocks, SSIU | 22 | 0 | 7.92 | 7.92
Racks
BLM | 4 | 2 | 7.68 | 7.68
BPM | 12 | 6 | 24.48 | 21.6
BTL/BAL | 3 | 1.5 | 0 | 0
Buncher | 0 | 0 | 0 | 0
Collimator Controls | 1 | 0.3 | 2.4 | 1.92
Computers, Front End | 3 | 1.5 | 3.6 | 2.16
Fast Dipole Switch | 1 | 0.1 | 16.6277 | 11.6394
Fiber Distribution | 3 | 1.5 | 3.1177 | 3.1177
General Data Acquisition | 52 | 37 | 196.0295 | 196.0295
General Instrumentation | 8 | 4 | 12.48 | 12.48
HB650 | 17 | 19.8 | 6.84 | 6.336
HWR | 6 | 7 | 2.4 | 2.4
Interlocks | 3 | 7.5 | 2.52 | 1.848
Ion Pump PS System | 2 | 0.6 | 14.4107 | 4.3232
LB650 | 25 | 32.2 | 10.56 | 9.804
LEBT | 5 | 2.5 | 85.2129 | 85.2129
Magnets, Dipole Corrector | 5 | 8.4 | 146.889 | 140.2918
Magnets, Dipole Corrector , Solenoids | 30 | 54.72 | 345.8559 | 297.4361
Magnets, Regular Quadrupole | 8 | 58.5 | 421.5119 | 383.4511
MEBT | 6 | 3 | 28.816 | 28.816
Motor Controllers | 7 | 3.5 | 8.4 | 8.4
MW, Laser Wire | 4 | 2 | 6.24 | 6.24
Network Room | 2 | 1 | 0.33255 | 0.33255
ODH | 1 | 2 | 0.84 | 0.84
RAW Absorber | 1 | 0 | 0.6 | 0.6
RF Interlocks | 0 | 0 | 0 | 0
RFQ | 0 | 0 | 0 | 0
RFQ, Buncher, HWR | 6 | 2.4 | 2.52 | 2.268
RFSeparator | 0 | 0 | 0 | 0
RFSep-BLBI | 1 | 0.5 | 1.56 | 1.56
RFSep-BLVac | 1 | 0.5 | 0 | 0
RFSep-Magnets, BLQuads | 2 | 0 | 0 | 0
RFSep-Magnets, Lambertson | 1 | 0 | 0 | 0
RFSep-Magnets, Vert. Dip. | 1 | 0 | 0 | 0
Spare | 0 | 0 | 0 | 0
SSR1 | 13 | 2.4 | 5.52 | 5.268
SSR2 | 25 | 7.2 | 10.56 | 9.804
Timing System | 2 | 1 | 3.6 | 3.6
WFE | 5 | 2.5 | 5.4 | 5.4
Wire Scanner | 2 | 1 | 3.84 | 3.84
Racks, Rittal
Cold Box Station | 1 | 0.5 | 3.6 | 3.6
General Data Acquisition | 36 | 3.6 | 17.28 | 17.28
PLC/LCW Controls | 1 | 0 | 0 | 0
Warm Compressor Section | 3 | 1.5 | 49.8831 | 49.8831
Reflected Power Loads
HB650 | 36 | 648 | 0 | 0
HWR | 8 | 8 | 0 | 0
LB650 | 36 | 396 | 0 | 0
SSR1 | 16 | 16 | 0 | 0
SSR2 | 35 | 140 | 0 | 0
Resonance Control
HB650 | 1 | 0.4 | 0.42 | 0.42
LB650 | 1 | 0.4 | 0.42 | 0.42
SSR1 | 1 | 0.4 | 0.42 | 0.42
Rittal Racks
PLC/LCW Controls | 4 | 2 | 2.4 | 2.4
RAW System | 1 | 0.5 | 0.6 | 0.6
RFQ | 4 | 2 | 2.4 | 2.4
Scrapers Vacuum Chamber
MEBT | 4 | 1.2 | 0 | 0
Skids
Dissolved Oxygen | 1 | 0.1 | 0.744 | 0.744
Ion Source | 1 | 0.4 | 2.4942 | 1.9953
RFQ | 3 | 109.36 | 68.6433 | 68.6433
Warm Compressor Section | 11 | 3717 | 1964.0071 | 1964.0071
Solenoids
LEBT | 4 | 30 | 0 | 0
Storage Tank
Cold Box Station | 1 | 0 | 4.9883 | 4.9883
Tank
Compressed Air | 1 | 0 | 0 | 0
LCW | 1 | 0 | 0 | 0
Valves
Insulating Vac | 22 | 0 | 0 | 0
Valves, Gate
HB650 | 1 | 0 | 0.036 | 0.036
HWR | 1 | 0 | 0.036 | 0.036
Valves, Right Angle
HB650 | 30 | 0 | 1.08 | 1.08
HWR | 5 | 0 | 0.18 | 0.18
LB650 | 45 | 0 | 1.62 | 1.62
RFSeparator | 4 | 0 | 0.144 | 0.144
SSR1 | 10 | 0 | 0.36 | 0.36
SSR2 | 35 | 0 | 1.26 | 1.26
Water/Oil Separator
Compressed Air | 1 | 0 | 0.6 | 0.6
Welding Receptacle
Cold Box Station | 1 | 0 | 49.8831 | 49.8831
Warm Compressor Section | 1 | 0 | 49.8831 | 49.8831
(blank)
General Data Acquisition | 13 | 6.5 | 7.8 | 7.8
Primary Reference Line | 1 | 0.4 | 0.42 | 0.42
(blank) |  | 0 | 0 | 0
Grand Total | 2523 | 13555.3333 | 20256.7691 | 18181.1191

## Requirements Data
-> Enter only relevant fields for items that take up floor space, require environmental control, cooling water, AC power, a rack, or networking. -> If equipment does not extend beyond the rack it does not need to be included. Including cables will allow us to determine equipment location based on access to power or networking. -> If multiple cable types run to the same rack select the least flexible cable type going to the rack and provide the total number of all cables. -> Columns D-H have a "red triangle" in the right-hand corner -- hoover the mouse over them to view addtional information.
|  | Room Data Sheet | [60 empty] | C_
PIP-II
= Denotes missing information
| #N/A | = These cells are automatically calculated, no input required
= Data cells not applicable
See Ryan's Tech Note for discussion
[14 empty] | Automatic filled out cells | [16 empty] | Automatic filled cells | [8 empty] | Automatic filled out cells |  |  | Automatic filled out cells | TN#https://web.fnal.gov/project/piptech/IC%20BldgI%20%20Electrical%20TN/Forms/AllItems.aspx
| Automatic filled out cells |  | Start Here ↓ | [8 empty] | Design Uncertainty |  |  | Spatial Requirements |  |  |  |  | Floor Requirements |  |  | Environmental | [5 empty] | Cooling | [7 empty] | AC Distribution | [13 empty] | Racks |  |  |  | Cables |  |  | Safety |  |  | Communication | NOTES
Identifier | WBS Level 2 | WBS ID | WBS Name | Building | Space Designation Location | Sub-System | User Defined Sub-System | Component | Description | Identifier - To Be Deleted | Quantity | Level of Design | Source of Requirements | Uncertainty Multiplier | Space Type | Length (in) | Width (in) | Height (in) | Weight (lbs) | Floor Flatness | Vibration | Finishes | Heating (F) | Cooling (F) | Humidity (%) | Pressurization Requirement | ODH (air changes/hr) | Any Special Ventilation (CFM) | Cooling Type | Heat Load (KW) | Total Heat Load (KW) | Heat Load to Air from Cables (KW) | Supply Nominal (F) | Supply Max (F) | Stability (F) | ΔT (F) | Power Requirement | Volts | Amps | Volt-Amperes | Total KVA | Power Factor (%) | Total Power (KW) | UPS (kVA / time (min)) | Standby Power (kVA) | Breaker (A) | Line Filter? | Dedicated Disconnect? | Special LOTO Provisions? | Special Grounding Required? | Size | Front Access | Closed Sides | Rear | Access to Power or Signal Cable Tray? | Cable Type | Count | Load greater than 50 V/100 A | Xrays? | ESS (Electrical Safety System) | Please select type of comm. | Other Requirements or Comments | Column1
DM-001 | 121.03 | 121.03.07 | Controls | LG | LG-BTL | Computers, Front End |  | Racks | Networking, permits etc. |  | 3 | Preliminary | Off the Shelf | 5% | Floor | 30 | 24 | 60 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 0.5 | 1.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 10 | 1200 | 3.6 | 60 | 2.16 | NA | NA | 20 | Yes | No | No | No | * 19"W/52U X 29" D | Open | Left AND Right | Closed | Yes | Flexible <1cm (e.g. RG58) | 2 | Yes | No | No | Ethernet | One rack requires two 120V-20A | C_Controls
DM-002 | 121.03 | 121.03.08 | SS | LG | LG-BTL | Interlocks |  | Racks | ESS interface |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 30 | 24 | 36 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 0.3 | 0.3 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 7 | 840 | 0.84 | 20 | 0.168 | NA | NA | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left Only | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 2 | Yes | No | Yes | Other (specify) | Requires additional "End Rack". Connection to Safety System Network | C_SS
DM-003 | 121.3 | 121.3.06 | Controls | F3 | BTL-F3 Building | PLC/LCW Controls |  | Racks, Rittal | Rittal half size cabinet |  | 1 | Preliminary | Off the Shelf | 5% | [16 empty] | 0 | [8 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_Controls
DM-004 | 121.03 | 121.03.06 | Vacuum | F3 | BTL-F3 Building | Ion Pump PS System |  | Racks | Bulk, Ion pump PS, gauge interface, network switch |  | 2 | Preliminary | Off the Shelf | 5% | Floor | 30 | 24 | 60 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 0.3 | 0.6 | [5 empty] | 208 V - 3 Phase - 3 Wire | 208 | 20 | 7205.3314 | 14.4107 | 30 | 4.3232 | NA | NA | 20 | No | No | No | No | 19"W/42U X 29" D | Open | Open | Closed | Yes | Flexible <1cm (e.g. RG58) | 4 | Yes | No | No | Ethernet | Located near LCW PLC controls. Additional 120V 10A circuit for network switch | C_Vacuum
DM-005 | 121.03 | 121.03.09 | Instrumentation | LG | LG-BTL | BPM |  | Racks |  |  | 2 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 60 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 0.5 | 1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 20 | 2400 | 4.8 | 60 | 2.88 | NA | NA | 20 | Yes | No | No | No | 19"W/52U X 29" D | Open | Open | Closed | Yes | Flexible <1cm (e.g. RG58) | 320 | Yes | No | No | Ethernet |  | C_Instrumentation
DM-006 | 121.03 | 121.03.09 | Instrumentation | F3 | BTL-F3 Building | BPM |  | Racks |  |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 60 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 20 | 2400 | 2.4 | 60 | 1.44 | NA | NA | 20 | Yes | No | No | No | 19"W/42U X 29" D | Open | Open | Closed | Yes | Flexible <1cm (e.g. RG58) | 320 | Yes | No | No | Ethernet |  | C_Instrumentation
DM-007 | 121.05 | 121.05.04 | BTLBAL | LG | LG-BTL | Collimator Controls |  | Racks | will this be needed?? |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 30 | 24 | 60 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 0.3 | 0.3 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 20 | 2400 | 2.4 | 80 | 1.92 | NA | NA | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Open | Closed | Yes | Flexible <1cm (e.g. RG58) | 21 | Yes | No | No | ACNET |  | C_BTLBAL
DM-008 | 121.03 | 121.03.05 | Magnets | F3 | BTL-F3 Building | Fast Dipole Switch |  | Racks | Pulse Magnet Power Supply |  | 1 | Conceptual | Expert Opinion | 50% | Floor | 30 | 24 | 60 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 0.1 | 0.1 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 20 | 16627.6878 | 16.6277 | 70 | 11.6394 | NA | NA | 20 | No | No | Yes | Yes | * 19"W/52U X 29" D | Open | Left AND Right | Closed | Yes | "Flexible" >1cm (e.g. 500MCM stranded) | 8 | Yes | No | Yes | Ethernet |  | C_Magnets
DM-009 | 121.03 | 121.03.05 | Magnets | LG | LG-BTL Power Supply | Fast Dipole Switch |  | Cables |  |  | 8 | Preliminary | Prototype-Testing | 25% | [14 empty] | Air, Environment |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | [12 empty] | "Flexible" >1cm (e.g. 500MCM stranded) | 8 | No | No | No |  |  | C_Magnets
DM-010 | 121.03 | 121.03.05 | Magnets | LG | LG-BTL Power Supply | Fast Dipole Switch |  | Magnets |  |  | 1 | Conceptual | Expert Opinion | 50% | [14 empty] | Air, Environment |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | [14 empty] | No | No | No |  |  | C_Magnets
DM-011 | 121.03 | 121.03.05 | Magnets | F3 | BTL-F3 Building | Magnets, Dipole |  | Power Supplies | TeV PS |  | 1 | Preliminary | Expert Opinion | 50% | Floor | 60 | 24 | 96 | 3500 |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | LCW | 12 | 12 | 3 | 90 | 105 | 1 |  | 480 V - 3 Phase - 3 Wire | 480 | 125 | 103923.0485 | 103.923 | 90 | 93.5307 | NA | NA | 125 | No | Yes | Yes | No | Other | Doors | Left AND Right | Closed | Yes | "Flexible" >1cm (e.g. 500MCM stranded) | 4 | Yes | No | Yes | Ethernet |  | C_Magnets
DM-012 | 121.03 | 121.03.05 | Magnets | Booster | Booster | Magnets, Dipole |  | Power Supplies | 125KW Spange PS |  | 2 | Preliminary | Off the Shelf | 5% | Floor | 62 | 44 | 89 | 3500 |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | LCW | 20 | 40 | 5 | 90 | 105 | 1 |  | 480 V - 3 Phase - 3 Wire | 480 | 200 | 166276.8775 | 332.5538 | 90 | 299.2984 | NA | NA | 200 | No | Yes | Yes | No | Other | Doors | Left AND Right | Closed | Yes | "Flexible" >1cm (e.g. 500MCM stranded) | 8 | Yes | No | Yes | Ethernet |  | C_Magnets
DM-013 | 121.03 | 121.03.05 | Magnets | BTL | BTL-Beamline Tunnel | Magnets, Dipole |  | Cables | Dipole cables |  | 20 | Preliminary | Off the Shelf | 5% | [14 empty] | Air, Environment |  | 0 | 0.65 | [7 empty] | 0 | 0 | 100 | 0 | [11 empty] | Yes | "Flexible" >1cm (e.g. 500MCM stranded) | 20 | No | No |  |  | Cables for line #24Dipole PS | C_Magnets
DM-014 | 121.03 | 121.03.05 | Magnets | BTL | BTL-Beamline Tunnel | Magnets, Dipole |  | Cables | Dipole cables |  | 16 | Preliminary | Off the Shelf | 5% | [14 empty] | Air, Environment |  | 0 | 2.2 | [7 empty] | 0 | 0 | 100 | 0 | [11 empty] | Yes | "Flexible" >1cm (e.g. 500MCM stranded) | 16 | No | No |  |  | Cables for line #25 Dipole PS | C_Magnets
DM-015 | 121.03 | 121.03.05 | Magnets | F3 | BTL-F3 Building | Magnets, Regular Quadrupole |  | Racks | Quadrupole Power Supplies |  | 3 | Preliminary | Off the Shelf | 5% | Floor | 30 | 24 | 90 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | Air, Environment | 10 | 30 | [5 empty] | 480Y/277 V - 3 Phase - 4 Wire | 480 | 60 | 49883.0633 | 149.6492 | 100 | 149.6492 |  |  | 60 |  | Yes |  | No | 19"W/42U X 29" D | Open | Left AND Right | Closed | Yes | "Flexible" >1cm (e.g. 500MCM stranded) | 56 | Yes | No | Yes | Ethernet | Four 480V-60A circuits, two 208V-15A circuits, two 120V 20A circuits | C_Magnets
DM-016 | 121.03 | 121.03.05 | Magnets | BTL | BTL-Beamline Tunnel | Magnets, Regular Quadrupole |  | Cables | Quad Cables |  | 32 | Conceptual | Off the Shelf | 5% | [14 empty] | Air, Environment |  | 0 | 3.1 | [7 empty] | 0 | 0 | 100 | 0 | [13 empty] | 32 | No | No |  |  |  | C_Magnets
DM-017 | 121.03 | 121.03.05 | Magnets | BTL | BTL-Beamline Tunnel | Magnets, Regular Quadrupole |  | Magnets |  |  | 57 | Conceptual | Prototype-Testing | 25% | [7 empty] | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  |  | LCW | 0.53 | 30.21 | 2.5 | 90 | 105 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No | No |  |  |  | C_Magnets
DM-018 | 121.03 | 121.03.05 | Magnets | BTL | BTL-Beamline Tunnel | Magnets, Regular Quadrupole |  | Magnets | Booster inj. C Mag. |  | 1 | Preliminary | Prototype-Testing | 25% | [7 empty] | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  |  | LCW | 6.1 | 6.1 | 0.6 | 90 | 105 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_Magnets
DM-019 | 121.03 | 121.03.05 | Magnets | F3 | BTL-F3 Building | Magnets, Dipole Corrector |  | Racks | CE Dipoles |  | 3 | Preliminary | Off the Shelf | 5% | Floor | 30 | 24 | 90 |  |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  |  | Air, Environment | 2 | 6 | [5 empty] | 480Y/277 V - 3 Phase - 4 Wire | 480 | 40 | 33255.3755 | 99.7661 | 100 | 99.7661 |  |  | 40 |  | Yes |  | No | 19"W/42U X 29" D |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 60 | Yes | No | No | Ethernet | One 208V-40A, Two 120V-20A | C_Magnets
DM-020 | 121.03 | 121.03.05 | Magnets | BTL | BTL-Beamline Tunnel | Magnets, Dipole Corrector |  | Cables |  |  | 56 | Preliminary | Off the Shelf | 5% | [14 empty] | Air, Environment |  | 0 | 3.6 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 56 | No | No |  |  |  | C_Magnets
DM-021 | 121.03 | 121.03.05 | Magnets | BTL | BTL-Beamline Tunnel | Magnets, Dipole Corrector |  | Magnets |  |  | 56 | Preliminary | Off the Shelf | 5% | [7 empty] | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  |  | Air, Environment | 0.1 | 5.6 | [8 empty] | 0 | 0 | 100 | 0 | [13 empty] | 56 | No | No |  |  |  | C_Magnets
DM-022 | 121.05 | 121.05.04 | BTLBAL | BAL Area | BAL-Beam Absorber | RAW Absorber |  | Pumps | Pumps |  | 1 | Preliminary | Prototype-Testing | 25% | [14 empty] | LCW | 75 | 75 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 5 | 4156.9219 | 4.1569 | 100 | 4.1569 |  |  |  |  | Yes | Yes | [8 empty] | Yes |  |  |  | 480V pump power | C_BTLBAL
DM-023 | 121.05 | 121.05.04 | BTLBAL | BAL Area | BAL-Beam Absorber | RAW Absorber |  | Racks | Controls |  | 1 | Preliminary | Prototype-Testing | 25% | [16 empty] | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 0.6 | 100 | 0.6 | [14 empty] | Yes |  |  |  | 120V control power | C_BTLBAL
DM-024 | N/A | N/A | Upgrades | LG | LG-Upgrade | RFSep- HPRF |  | Power Amplifiers | SCL SS-70kW style |  | 1 | Pre-conceptual | Expert Opinion | 50% | Floor | 96 | 134 | 96 |  |  |  |  | 40-95F | 82 +/-4 |  |  |  |  | LCW | 103.9909 | 103.9909 |  | 88 | 92 | 4 | 7.2 | 480Y/277 V - 3 Phase - 4 Wire | 480 | 248.6 | 206682.1588 | 206.6822 | 86 | 177.7467 |  | NA | 450 | No | Yes | No | No | Other | Open | Left AND Right | Closed | Yes | Rigid (e.g. hardline coax) | 10 | Yes | No | Yes | ACNET |  | C_Upgrades
DM-025 | N/A | N/A | Upgrades | LG | LG-Upgrade | RFSep-Magnets, Vert. Dip. |  | Racks | Need 2 vert. dip. corrector (SCL dip.-style PS) |  | 1 | Pre-conceptual | Expert Opinion | 50% | Floor | 32 | 24 | 96 |  |  | No |  | 78 +/-5 | 78 +/-5 | 55 |  |  | 900 | Air, Environment | 0 | 0 | [8 empty] | 0 | 0 |  | 0 | [7 empty] | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) |  | No | No | Yes | Ethernet |  | C_Upgrades
DM-026 | N/A | N/A | Upgrades | LG | LG-Upgrade | RFSep-Magnets, Vert. Dip. |  | Power Supplies | Need 2 vert. dip. corrector (SCL dip.-style PS) |  | 2 | Pre-conceptual | Expert Opinion | 50% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 |  |  |  |  | 0.5 | 1 | 0.04 |  |  |  |  | 480Y/277 V - 3 Phase - 4 Wire | 480 | 10 | 8313.8439 | 16.6277 | 86 | 14.2998 | NA | NA | 20 | TBD | TBD | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 12 | Yes | No | Yes | Ethernet |  | C_Upgrades
DM-027 | N/A | N/A | Upgrades | LG | LG-Upgrade | RFSep-Magnets, Lambertson |  | Racks | Need 3 (SCL quad-style PS) |  | 1 | Pre-conceptual | Expert Opinion | 50% | Floor | 32 | 24 | 96 |  |  | No |  | 78 +/-5 | 78 +/-5 | 55 |  |  | 900 | Air, Environment | 0 | 0 | [8 empty] | 0 | 0 | 86 | 0 | [7 empty] | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 18 | No | No | Yes | Ethernet |  | C_Upgrades
DM-028 | N/A | N/A | Upgrades | LG | LG-Upgrade | RFSep-Magnets, Lambertson |  | Power Supplies | Need 3 (SCL quad-style PS) |  | 3 | Pre-conceptual | Expert Opinion | 50% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 |  |  |  |  | 0.5 | 1.5 | 3.5 |  |  |  |  | 480Y/277 V - 3 Phase - 4 Wire | 480 | 10 | 8313.8439 | 24.9415 | 84 | 20.9509 | NA | NA | 15 | TBD | TBD | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 18 | Yes | No | Yes | Ethernet |  | C_Upgrades
DM-029 | N/A | N/A | Upgrades | LG | LG-Upgrade | RFSep-Spang |  | Power Supplies | 75KW Spange PS |  | 5 | Preliminary | Off the Shelf | 5% | Floor | 31.5 | 24 | 51 | 645 |  |  | Sealed concrete | 65 +/-10 | 75 +/-10 | 0-90 |  |  | 0 | LCW | 12 | 60 | 3 | 90 | 105 | 1 |  | 480 V - 3 Phase - 3 Wire | 480 | 125 | 103923.0485 | 519.6152 | 90 | 467.6537 | NA | NA | 125 | No | Yes | Yes | No | Other | Doors | Left AND Right | Closed | Yes | "Flexible" >1cm (e.g. 500MCM stranded) | 4 | Yes | No | Yes | Ethernet |  | C_Upgrades
DM-030 | N/A | N/A | Upgrades | LG | LG-Upgrade | RFSep-Magnets, BLQuads |  | Racks | Need 8 Quad PS - SCL quad-style PS |  | 2 | Pre-conceptual | Expert Opinion | 50% | Floor | 32 | 24 | 96 |  |  | No |  | 78 +/-5 | 78 +/-5 | 55 |  |  | 900 | Air, Environment |  | 0 | [8 empty] | 0 | 0 | 84 | 0 | NA | NA | 15 | TBD | TBD | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 18 | No | No | Yes | Ethernet |  | C_Upgrades
DM-031 | N/A | N/A | Upgrades | LG | LG-Upgrade | RFSep-Magnets, BLQuads |  | Power Supplies | Need 8 Quad PS - SCL quad-style PS |  | 8 | Pre-conceptual | Expert Opinion | 50% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 |  |  |  |  | 0.5 | 4 | 3.5 |  |  |  |  | 480Y/277 V - 3 Phase - 4 Wire | 480 | 10 | 8313.8439 | 66.5108 | 84 | 55.869 | NA | NA | 15 | TBD | TBD | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 143 | Yes | No | Yes | Ethernet |  | C_Upgrades
DM-032 | N/A | N/A | Upgrades | LG | LG-Upgrade | RFSep-BLVac |  | Racks | Rack Contains all Ion Pump Controllers, Turbo Pump Controlers, Gauge readbacks |  | 1 | Pre-conceptual | Expert Opinion | 50% | Floor | 24 | 32 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire |  |  | 0 | 0 | 100 | 0 | [7 empty] | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes |  | 4 | No |  |  | Ethernet | Additional 120V 10A circuit for network switch | C_Upgrades
DM-033 | N/A | N/A | Upgrades | LG | LG-Upgrade | RFSep-BLVac |  | Power Supplies |  |  | 1 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 24 | 13 | 540.3999 | 0.5404 | 100 | 0.5404 | [12 empty] | Semi-rigid >1cm (e.g. 0.5" Heliax) |  | No |  |  |  | Rack Power supply (I may be doubling the load from the rack equipment) | C_Upgrades
DM-034 | N/A | N/A | Upgrades | LG | LG-Upgrade | RFSep-BLBI |  | Racks | General Rack for BI instruments |  | 1 | Pre-conceptual | Expert Opinion | 50% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 13 | 1560 | 1.56 | 100 | 1.56 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 20 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Upgrades
DN-001 | 121.02 | 121.02.06 | CDS | LG | LG-HWR | General Data Acquisition |  | Racks, Rittal |  |  | 3 | Preliminary | Prototype-Testing | 25% | Floor | 64 | 16 | 84 |  |  |  |  | 72 +/- 5 | 72 +/- 5 |  |  |  |  | Air, Environment | 0.1 | 0.3 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 1.44 | 100 | 1.44 |  |  | 20 | TBD | No | No | N/A | Other | Doors | Left AND Right | Closed | Yes | Flexible <1cm (e.g. RG58) | 3400 | Yes | No | No | Ethernet |  | C_CDS
DN-002 | 121.02 | 121.02.06 | CDS | LG | LG-SSR1 | General Data Acquisition |  | Racks, Rittal |  |  | 4 | Preliminary | Prototype-Testing | 25% | Floor | 64 | 16 | 84 |  |  |  |  | 72 +/- 5 | 72 +/- 5 |  |  |  |  | Air, Environment | 0.1 | 0.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 1.92 | 100 | 1.92 |  |  | 20 | TBD | No | No | N/A | Other | Doors | Left AND Right | Closed | Yes | Flexible <1cm (e.g. RG58) | 3400 | Yes | No | No | Ethernet |  | C_CDS
DN-003 | 121.02 | 121.02.06 | CDS | LG | LG-SSR2 | General Data Acquisition |  | Racks, Rittal |  |  | 10 | Preliminary | Prototype-Testing | 25% | Floor | 64 | 16 | 84 |  |  |  |  | 72 +/- 5 | 72 +/- 5 |  |  |  |  | Air, Environment | 0.1 | 1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 4.8 | 100 | 4.8 |  |  | 20 | TBD | No | No | N/A | Other | Doors | Left AND Right | Closed | Yes | Flexible <1cm (e.g. RG58) | 3400 | Yes | No | No | Ethernet |  | C_CDS
DN-004 | 121.02 | 121.02.06 | CDS | LG | LG-LB650 | General Data Acquisition |  | Racks, Rittal |  |  | 11 | Preliminary | Prototype-Testing | 25% | Floor | 64 | 16 | 84 |  |  |  |  | 72 +/- 5 | 72 +/- 5 |  |  |  |  | Air, Environment | 0.1 | 1.1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 5.28 | 100 | 5.28 |  |  | 20 | TBD | No | No | N/A | Other | Doors | Left AND Right | Closed | Yes | Flexible <1cm (e.g. RG58) | 3400 | Yes | No | No | Ethernet |  | C_CDS
DN-005 | 121.02 | 121.02.06 | CDS | LG | LG-HB650 | General Data Acquisition |  | Racks, Rittal |  |  | 8 | Preliminary | Prototype-Testing | 25% | Floor | 64 | 16 | 84 |  |  |  |  | 72 +/- 5 | 72 +/- 5 |  |  |  |  | Air, Environment | 0.1 | 0.8 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 3.84 | 100 | 3.84 |  |  | 20 | TBD | No | No | N/A | Other | Doors | Left AND Right | Closed | Yes | Flexible <1cm (e.g. RG58) | 3400 | Yes | No | No | Ethernet |  | C_CDS
DN-006 | 121.02 | 121.02.06 | CDS | LG | LG-HWR | General Data Acquisition |  | Racks | Control Racks for CDS |  | 2 | Preliminary | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 72 +/- 5 | 72 +/- 5 |  |  |  |  | Air, Environment | 1 | 2 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 208 | 15 | 5403.9985 | 10.808 | 100 | 10.808 |  |  | 20 | TBD | No | No | N/A | * 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 1000 | Yes | No | No | Ethernet | Still working with Cryo on the details of these racks | C_CDS
DN-007 | 121.02 | 121.02.06 | CDS | LG | LG-SSR1 | General Data Acquisition |  | Racks | Control Racks for CDS |  | 2 | Preliminary | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 72 +/- 5 | 72 +/- 5 |  |  |  |  | Air, Environment | 1 | 2 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 208 | 15 | 5403.9985 | 10.808 | 100 | 10.808 |  |  | 20 | TBD | No | No | N/A | * 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 1000 | Yes | No | No | Ethernet | Still working with Cryo on the details of these racks | C_CDS
DN-008 | 121.02 | 121.02.06 | CDS | LG | LG-SSR2 | General Data Acquisition |  | Racks | Control Racks for CDS |  | 6 | Preliminary | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 72 +/- 5 | 72 +/- 5 |  |  |  |  | Air, Environment | 1 | 6 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 208 | 15 | 5403.9985 | 32.424 | 100 | 32.424 |  |  | 20 | TBD | No | No | N/A | * 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 1000 | Yes | No | No | Ethernet | Still working with Cryo on the details of these racks | C_CDS
DN-009 | 121.02 | 121.02.06 | CDS | LG | LG-LB650 | General Data Acquisition |  | Racks | Control Racks for CDS |  | 7 | Preliminary | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 72 +/- 5 | 72 +/- 5 |  |  |  |  | Air, Environment | 1 | 7 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 208 | 15 | 5403.9985 | 37.828 | 100 | 37.828 |  |  | 20 | TBD | No | No | N/A | * 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 1000 | Yes | No | No | Ethernet | Still working with Cryo on the details of these racks | C_CDS
DN-010 | 121.02 | 121.02.06 | CDS | LG | LG-HB650 | General Data Acquisition |  | Racks | Control Racks for CDS |  | 5 | Preliminary | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 72 +/- 5 | 72 +/- 5 |  |  |  |  | Air, Environment | 1 | 5 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 208 | 15 | 5403.9985 | 27.02 | 100 | 27.02 |  |  | 20 | TBD | No | No | N/A | * 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 1000 | Yes | No | No | Ethernet | Still working with Cryo on the details of these racks | C_CDS
DN-011 | 121.03 | 121.03.07 | Controls | LG | LG-General | General Data Acquisition |  | Racks | needs distribution along gallery |  | 27 | Conceptual | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 9 | Air, Environment | 0.5 | 13.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 48.6 | 100 | 48.6 |  |  | 20 | Yes | No | No | TBD | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 200 | Yes | No | No | Ethernet | If VOIP phones then need UPS | C_Controls
DN-012 | 121.03 | 121.03.07 | Controls | LG | LG-General | Motor Controllers |  | Racks | needs distribution along gallery |  | 7 | Conceptual | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 9 | Air, Environment | 0.5 | 3.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 10 | 1200 | 8.4 | 100 | 8.4 |  |  | 20 | Yes | No | No | TBD | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 100 | Yes | No | No | Ethernet | Motor controllers need 2x20 amp breakers | C_Controls
DN-013 | 121.03 | 121.03.07 | Controls | HBB | HBB-Control Room | Timing System |  | Racks |  |  | 2 | Preliminary | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 9 | Air, Environment | 0.5 | 1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 3.6 | 100 | 3.6 |  |  | 20 | Yes | No | No | TBD | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 100 | Yes | No | No | Ethernet |  | C_Controls
DN-014 | 121.03 | 121.03.07 | Controls | UP | UP | PLC/LCW Controls |  | Rittal Racks | 1 Rittal rack per LCW system |  | 4 | Preliminary | Off the Shelf | 5% | Floor | 40 | 16 | 78 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 9 | Air, Environment | 0.5 | 2 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 2.4 | 100 | 2.4 |  |  | 20 | Yes | No | No | N/A | Other | Doors | Left AND Right | Closed |  | Flexible <1cm (e.g. RG58) | 100 | Yes | No | No | Ethernet | 1 rack per LCW system | C_Controls
DN-015 | 121.03 | 121.03.07 | Controls | BAL Area | BAL-Beam Absorber | RAW System |  | Rittal Racks | Rittal rack |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 64 | 16 | 84 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  |  | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 0.6 | 100 | 0.6 |  |  | 20 | Yes | No | No | N/A | Other | Doors | Left AND Right | Closed |  | Flexible <1cm (e.g. RG58) | 100 | Yes | No | No | Ethernet |  | C_Controls
DN-016 | 121.03 | 121.03.07 | Controls | HBB | HBB-Computer Space | Fiber Distribution |  | Racks |  |  | 3 | Conceptual | Off the Shelf | 5% | Floor | 32 | 24 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  |  | Air, Environment | 0.5 | 1.5 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 120 | 5 | 1039.2305 | 3.1177 | 100 | 3.1177 |  |  | 20 | Yes | No | No | TBD | 19"W/60U X 29" D | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 10 | Yes | No | No | Other (specify) | Feed through only no comm. needed | C_Controls
DN-017 | 121.03 | 121.03.07 | Controls | CP | UP | General Data Acquisition |  | Racks |  |  | 1 | Conceptual | Prototype-Testing | 25% | Floor | 32 | 24 | 78 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | Yes | No | No | TBD | 19"W/60U X 29" D | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 10 | Yes | No | No | Ethernet |  | C_Controls
DN-018 | 121.03 | 121.03.07 | Controls | CP | Cryoplant Building | General Data Acquisition |  | Racks |  |  | 1 | Conceptual | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | Yes | No | No | TBD | 19"W/60U X 29" D | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 10 | Yes | No | No | Ethernet |  | C_Controls
DN-019 | 121.03 | 121.03.05 | Magnets | LG | LG-BTL | General Data Acquisition |  | Racks |  |  | 1 | Conceptual | Prototype-Testing | 25% | Floor | 32 | 24 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 30 | 24941.5316 | 24.9415 | 100 | 24.9415 |  |  | 20 | Yes | No | No | TBD | 19"W/60U X 29" D | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 10 | Yes | No | No | Ethernet |  | C_Magnets
DN-020 | 121.03 | 121.03.07 | Controls | LG | LG-General | Computers, Console |  | Consoles, Fixed |  |  | 10 | Preliminary | Expert Opinion | 50% | Rack Mounted | 32 | 24 | 36 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  |  | Air, Environment | 0.05 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 4.8 | 100 | 4.8 |  |  | 20 | No | No | No | No | Other |  |  |  |  | Flexible <1cm (e.g. RG58) | 5 | Yes | No | No | ACNET, WIFI |  | C_Controls
DN-021 | 121.03 | 121.03.07 | Controls | LG | LG-General | Computers, Console |  | Consoles, Mobile |  |  | 10 | Preliminary | Expert Opinion | 50% | Floor | 32 | 24 | 36 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  |  | Air, Environment | 0.06 | 0.6 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 4.8 | 100 | 4.8 |  |  | 20 | No | No | No | No | Other |  |  |  |  | Flexible <1cm (e.g. RG58) | 5 | Yes | No | No | ACNET, WIFI |  | C_Controls
DN-022 | 121.03 | 121.03.07 | Controls | HBB | HBB-Control Room | Computers, Console |  | Consoles, Fixed |  |  | 3 | Preliminary | Expert Opinion | 50% | Floor | 32 | 24 | 36 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  |  | Air, Environment | 0.06 | 0.18 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 1.44 | 100 | 1.44 |  |  | 20 | No | No | No | No | Other |  |  |  |  | Flexible <1cm (e.g. RG58) | 6 | Yes | No | No | ACNET, WIFI |  | C_Controls
DN-023 | 121.03 | 121.03.03 | HPRF | LG | LG-HWR | HWR |  | Racks | HWR amplifiers are mounted in these racks along with PLC. HLA is represented here as well. |  | 4 | Final | Off the Shelf | 5% | Floor | [13 empty] | Air, Environment | 1.75 | 7 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 2.4 | 100 | 2.4 | [7 empty] | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Rigid (e.g. hardline coax) | 40 | Yes | No | Yes | ACNET | Suspect at most 2 in a rack Fewest # is 4 if only used for HPRF HWR-1 208 3phase 3 wire, HWR2-8 480 3phase 4 wire. | C_HPRF
DN-024 | 121.03 | 121.03.07 | Controls | LG | LG-General | General Data Acquisition | LCW/Vacumm controls readbacks |  |  |  | 13 | Preliminary | Expert Opinion | 50% | Floor | 64 | 16 | 84 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  |  | Air, Environment | 0.5 | 6.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 7.8 | 100 | 7.8 |  |  | 20 | Yes | No | No | N/A | Other | Doors | Left AND Right | Closed | Yes | Flexible <1cm (e.g. RG58) | 100 | Yes | No | No | Ethernet | Additonal Rittal racks for LCW/Vacuum | C_Controls
DN-025 | 121.03 | 121.03.07 | Controls | HBB | HBB-Lower High Bay | RFQ |  | Rittal Racks | PLC/LCW Controls - 1 Rittal rack per LCW system |  | 4 | Preliminary | Off the Shelf | 5% | Floor | 64 | 16 | 84 |  |  |  |  | 75 +/- 5 | 75 +/- 5 |  |  |  |  | Air, Environment | 0.5 | 2 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 2.4 | 100 | 2.4 |  |  | 20 | Yes | No | No | N/A | Other | Doors | Left AND Right | Closed | Yes | Flexible <1cm (e.g. RG58) | 100 | Yes | No | No | Ethernet | 1 rack per LCW system | C_Controls
DN-026 | 121.03 | 121.03.03 | HPRF | LG | LG-HWR | HWR |  | Power Amplifiers |  |  | 8 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 40-95F | 82 +/-4 |  |  |  |  | LCW | 8.2855 | 66.2836 |  | 86 | 90 | 4 |  | 480Y/277 V - 3 Phase - 4 Wire | 480 | 21.2618 | 17676.7677 | 141.4141 | 90 | 127.2727 |  | NA | 30 | No | Yes | No | No | Other | Open | Left AND Right | Closed | Yes | Rigid (e.g. hardline coax) | 10 | Yes | No | Yes | ACNET |  | C_HPRF
DN-027 | 121.03 | 121.03.03 | HPRF | LG | LG-HWR | HWR |  | Circulators |  |  | 8 | Final | Off the Shelf | 5% | Suspended |  |  |  | 350 | [9 empty] | LCW | 0 | 0 |  | 86 | 90 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [13 empty] | 414 | No |  |  |  | Cable count is scaled via CMTS1, held here as placeholder | C_HPRF
DN-028 | 121.03 | 121.03.03 | HPRF | LG | LG-HWR | HWR |  | Reflected Power Loads |  |  | 8 | Final | Off the Shelf | 5% | Suspended |  |  |  | 16 | [9 empty] | LCW | 1 | 8 |  | 86 | 90 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_HPRF
DN-029 | 121.03 | 121.03.03 | HPRF | LG | LG-SSR1 | SSR1 |  | Racks |  |  | 5 | Preliminary | Prototype-Testing | 25% | Floor | 24 | 32 | 96 | [10 empty] | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 3 | 100 | 3 | [7 empty] | 19"W/60U X 29" D | Open | Left AND Right | Door | Yes | Rigid (e.g. hardline coax) | 40 | Yes | No | Yes | ACNET |  | C_HPRF
DN-030 | 121.03 | 121.03.03 | HPRF | LG | LG-SSR1 | SSR1 |  | Power Amplifiers |  |  | 16 | Final | Off the Shelf | 5% | Floor | [7 empty] | 40-95F | 82 +/-4 |  |  |  |  | LCW | 8.2855 | 132.5673 |  | 88 | 92 | 4 | 7.1 | 480Y/277 V - 3 Phase - 4 Wire | 480 | 21.2618 | 17676.7677 | 282.8283 | 90 | 254.5455 |  | NA | 40 | No | Yes | No | No | Other | Open | Left AND Right | Closed | Yes | Rigid (e.g. hardline coax) | 10 | Yes | No | Yes | ACNET |  | C_HPRF
DN-031 | 121.03 | 121.03.03 | HPRF | LG | LG-SSR1 | SSR1 |  | Power Amplifiers | HLA for SSR1 |  | 0 | Final | Off the Shelf | 5% | [14 empty] | Air, Environment | 0.62364 | 14.9673 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_HPRF
DN-032 | 121.03 | 121.03.03 | HPRF | LG | LG-SSR1 | SSR1 |  | Circulators |  |  | 16 | Final | Off the Shelf | 5% | Suspended |  |  |  | 350 | [9 empty] | LCW | 0 | 0 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [13 empty] | 658 | No |  |  |  | Cable count is scaled via CMTS1, held here as placeholder | C_HPRF
DN-033 | 121.03 | 121.03.03 | HPRF | LG | LG-SSR1 | SSR1 |  | Reflected Power Loads |  |  | 16 | Final | Off the Shelf | 5% | Suspended |  |  |  | 16 | [9 empty] | LCW | 1 | 16 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_HPRF
DN-034 | 121.03 | 121.03.03 | HPRF | LG | LG-SSR2 | SSR2 |  | Racks | Control equipment rack for PLCs |  | 5 | Preliminary | Expert Opinion | 50% | Floor | [13 empty] | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 3 | 100 | 3 | [7 empty] | 19"W/60U X 29" D | Doors | Left AND Right | Door | Yes | Rigid (e.g. hardline coax) | 40 | Yes | No | Yes | ACNET |  | C_HPRF
DN-035 | 121.03 | 121.03.03 | HPRF | LG | LG-SSR2 | SSR2 |  | Power Amplifiers |  |  | 35 | Conceptual | Expert Opinion | 50% | Floor | 72 | 48 | 96 |  |  |  |  | 40-95F | 82 +/-4 |  |  |  |  | LCW | 23.6727 | 828.5455 |  | 88 | 92 | 4 | 8.1 | 480Y/277 V - 3 Phase - 4 Wire | 480 | 60.7481 | 50505.0505 | 1767.6768 | 90 | 1590.9091 |  | NA | 120 | No | Yes | No | No | Other | Open | Left AND Right | Closed | Yes | Rigid (e.g. hardline coax) | 10 | Yes | No | Yes | ACNET |  | C_HPRF
DN-036 | 121.03 | 121.03.03 | HPRF | LG | LG-SSR2 | SSR2 |  | Power Amplifiers | HLA for SSR2 |  | 0 | Conceptual | Expert Opinion | 50% | [14 empty] | Air, Environment | 1.7818 | 62.3636 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | This item is only for the HLA component of the power amplifiers | C_HPRF
DN-037 | 121.03 | 121.03.03 | HPRF | LG | LG-SSR2 | SSR2 |  | Circulators |  |  | 35 | Preliminary | Expert Opinion | 50% | Suspended |  |  |  | 350 | [9 empty] | LCW | 0 | 0 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [13 empty] | 2113 | No |  |  |  | Cable count is scaled via CMTS1, held here as placeholder | C_HPRF
DN-038 | 121.03 | 121.03.03 | HPRF | LG | LG-SSR2 | SSR2 |  | Reflected Power Loads |  |  | 35 | Preliminary | Off the Shelf | 5% | Suspended |  |  |  | 16 | [9 empty] | LCW | 4 | 140 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_HPRF
DN-039 | 121.03 | 121.03.03 | HPRF | LG | LG-LB650 | LB650 |  | Racks | Control equipment rack for PLCs |  | 5 | Preliminary | Expert Opinion | 50% | Floor | [13 empty] | Air, Environment | 5 | 25 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 3 | 100 | 3 | [7 empty] | 19"W/60U X 29" D | Doors | Left AND Right | Door | Yes | Rigid (e.g. hardline coax) | 40 | Yes | No | Yes | ACNET |  | C_HPRF
DN-040 | 121.03 | 121.03.03 | HPRF | LG | LG-LB650 | LB650 |  | Power Amplifiers | 40 kW |  | 36 | Preliminary | Prototype-Testing | 25% | Floor | 72 | 134 | 96 |  |  |  |  | 40-95F | 82 +/-4 | na |  |  |  | LCW | 47.3455 | 1704.4364 |  | 88 | 92 | 4 | 7.2 | 480Y/277 V - 3 Phase - 4 Wire | 480 | 127.1473 | 105708.2452 | 3805.4968 | 86 | 3272.7273 |  | NA | 240 | No | Yes | No | No | Other | Open | Left AND Right | Closed | Yes | Rigid (e.g. hardline coax) | 10 | Yes | No | Yes | ACNET |  | C_HPRF
DN-041 | 121.03 | 121.03.03 | HPRF | LG | LG-LB650 | LB650 |  | Power Amplifiers | HLA for 40 kW |  | 0 | Pre-conceptual | Prototype-Testing | 25% | [14 empty] | Air, Environment | 3.5636 | 128.2909 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | This item is only for the HLA component of the power amplifiers | C_HPRF
DN-042 | 121.03 | 121.03.03 | HPRF | LG | LG-LB650 | LB650 |  | Circulators |  |  | 36 | Preliminary | Prototype-Testing | 25% | Suspended |  |  |  | 350 | [9 empty] | LCW | 0 | 0 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [13 empty] | 3118 | No |  |  |  | Cable count is scaled via CMTS1, held here as placeholder | C_HPRF
DN-043 | 121.03 | 121.03.03 | HPRF | LG | LG-LB650 | LB650 |  | Reflected Power Loads |  |  | 36 | Preliminary | Off the Shelf | 5% | Suspended |  |  |  | 17 | [9 empty] | LCW | 11 | 396 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_HPRF
DN-044 | 121.03 | 121.03.03 | HPRF | LG | LG-HB650 | HB650 |  | Racks | Control equipment rack for PLCs |  | 3 | Preliminary | Expert Opinion | 50% | Floor | [13 empty] | Air, Environment | 5 | 15 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 1.8 | 100 | 1.8 | [7 empty] | 19"W/60U X 29" D | Doors | Left AND Right | Door | Yes | Rigid (e.g. hardline coax) | 40 | Yes | No | Yes | ACNET |  | C_HPRF
DN-045 | 121.03 | 121.03.03 | HPRF | LG | LG-HB650 | HB650 |  | Power Amplifiers | 70 kW |  | 36 | Preliminary | Expert Opinion | 50% | Floor | 96 | 134 | 96 |  |  |  |  | 40-95F | 82 +/-4 |  |  |  |  | LCW | 103.9909 | 3743.6727 |  | 88 | 92 | 4 | 7.2 | 480Y/277 V - 3 Phase - 4 Wire | 480 | 254.2945 | 211416.4905 | 7610.9937 | 86 | 6545.4545 |  | NA | 450 | No | Yes | No | No | Other | Open | Left AND Right | Closed | Yes | Rigid (e.g. hardline coax) | 10 | Yes | No | Yes | ACNET |  | C_HPRF
DN-046 | 121.03 | 121.03.03 | HPRF | LG | LG-HB650 | HB650 |  | Power Amplifiers | HLA for 70 kW |  | 0 | Pre-conceptual | Expert Opinion | 50% | [14 empty] | Air, Environment | 6.2364 | 224.5091 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | This item is only for the HLA component of the power amplifiers | C_HPRF
DN-047 | 121.03 | 121.03.03 | HPRF | LG | LG-HB650 | HB650 |  | Circulators |  |  | 36 | Preliminary | Expert Opinion | 50% | Suspended |  |  |  | 350 | [9 empty] | LCW | 0 | 0 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [13 empty] | 1240 | No |  |  |  | Cable count is scaled via CMTS1, held here as placeholder | C_HPRF
DN-048 | 121.03 | 121.03.03 | HPRF | LG | LG-HB650 | HB650 |  | Reflected Power Loads |  |  | 36 | Preliminary | Off the Shelf | 5% | Suspended |  |  |  | 17 | [9 empty] | LCW | 18 | 648 |  | 88 | 92 | 4 |  |  |  |  | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_HPRF
DN-049 | 121.03 | 121.03.09 | Instrumentation | HBB | HBB-Upper High Bay | General Instrumentation |  | Racks | WFE |  | 5 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 2.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 13 | 1560 | 7.8 | 100 | 7.8 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 20 | Yes | No | No | Ethernet | Currently 4 at PIP2IT but they are filling | C_Instrumentation
DN-050 | 121.03 | 121.03.09 | Instrumentation | LG | LG-SSR1 | General Instrumentation |  | Racks |  |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 13 | 1560 | 1.56 | 100 | 1.56 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 20 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-051 | 121.03 | 121.03.09 | Instrumentation | LG | LG-HWR | BPM |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 1.92 | 100 | 1.92 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 172 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-052 | 121.03 | 121.03.09 | Instrumentation | LG | LG-SSR1 | BPM |  | Racks |  |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 1.92 | 100 | 1.92 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 172 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-053 | 121.03 | 121.03.09 | Instrumentation | LG | LG-SSR2 | BPM |  | Racks |  |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 1.92 | 100 | 1.92 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 172 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-054 | 121.03 | 121.03.09 | Instrumentation | LG | LG-SSR2 | BLM |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 1.92 | 100 | 1.92 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 186 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-055 | 121.03 | 121.03.09 | Instrumentation | LG | LG-SSR2 | MW, Laser Wire |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 2 | Preliminary | Expert Opinion | 50% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 13 | 1560 | 3.12 | 100 | 3.12 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 20 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-056 | 121.03 | 121.03.09 | Instrumentation | LG | LG-LB650 | General Instrumentation |  | Racks |  |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 13 | 1560 | 1.56 | 100 | 1.56 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 20 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-057 | 121.03 | 121.03.09 | Instrumentation | LG | LG-LB650 | BPM |  | Racks |  |  | 2 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 3.84 | 100 | 3.84 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 172 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-058 | 121.03 | 121.03.09 | Instrumentation | LG | LG-HB650 | BPM |  | Racks |  |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 1.92 | 100 | 1.92 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 172 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-059 | 121.03 | 121.03.09 | Instrumentation | LG | LG-HB650 | BLM |  | Racks |  |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 1.92 | 100 | 1.92 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 186 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-060 | 121.03 | 121.03.09 | Instrumentation | LG | LG-LB650 | MW, Laser Wire |  | Racks |  |  | 1 | Preliminary | Expert Opinion | 50% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 13 | 1560 | 1.56 | 100 | 1.56 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 20 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-061 | 121.03 | 121.03.09 | Instrumentation | LG | LG-HB650 | MW, Laser Wire |  | Racks |  |  | 1 | Preliminary | Expert Opinion | 50% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 13 | 1560 | 1.56 | 100 | 1.56 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 20 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-062 | 121.03 | 121.03.09 | Instrumentation | LG | LG-BTL | General Instrumentation |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 13 | 1560 | 1.56 | 100 | 1.56 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 20 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-063 | 121.03 | 121.03.09 | Instrumentation | LG | LG-BTL | BPM |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 3 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 1.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 5.76 | 100 | 5.76 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 172 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-064 | 121.03 | 121.03.09 | Instrumentation | LG | LG-BTL | BLM |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 2 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 3.84 | 100 | 3.84 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 186 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-065 | 121.03 | 121.03.09 | Instrumentation | HBB | HBB-Lower High Bay | Laser Wire |  | Laser Room | Primary Laser Rm |  | 1 | Preliminary | Expert Opinion | 50% | Floor | 216 | 180 | 96 |  |  |  |  | 75 +/-3 | 75 +/-3 |  |  |  |  | Air, Environment |  | 0 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 208 | 15 | 5403.9985 | 5.404 | 100 | 5.404 | [7 empty] | Other | [6 empty] | Yes |  |  |  | Laser Rooms parameters are unknown | C_Instrumentation
DN-066 | 121.03 | 121.03.09 | Instrumentation | LG | LG-HB650 | Laser Wire |  | Laser Room | Secondary Laser Rm |  | 1 | Preliminary | Expert Opinion | 50% | Floor | 216 | 180 | 96 |  |  |  |  | 75 +/-3 | 75 +/-3 | [6 empty] | 0 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 208 | 15 | 5403.9985 | 5.404 | 100 | 5.404 | [7 empty] | Other | [6 empty] | Yes |  |  |  | Laser Rooms parameters are unknown | C_Instrumentation
DN-067 | 121.03 | 121.03.09 | Instrumentation | LG | LG-BTL | Wire Scanner |  | Racks | Rack distributed throughout any of the gallery locations listed |  | 2 | Preliminary | Prototype-Testing | 25% | Floor | 30 | 24 | 96 |  |  |  |  | 82 +/- 5 | 82 +/- 5 |  |  | 0 | 9 | Air, Environment | 0.5 | 1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 16 | 1920 | 3.84 | 100 | 3.84 | na | na | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 40 | Yes | No | No | Ethernet | Grouping in sections GI, BPM, BLM, LW…. | C_Instrumentation
DN-068 | 121.03 | 121.03.04 | LLRF | HBB | HBB-Upper High Bay | Primary Reference Line |  |  | MO/PRL - 4x4x1 MO+ 36U rack |  | 1 | Final | Prototype-Testing | 30% | Floor, Suspended | 84 | 48 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0.42 | 100 | 0.42 | .4/120 | 0.4 | 20 | Yes |  |  |  | Other | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 16 | Yes | N/A | N/A | ACNET | Wall Mounted Tunnel side @ beginning of frequecy section. Direct access to tunnel (penetration) | C_LLRF
DN-069 | 121.03 | 121.03.04 | LLRF | HBB | HBB-Upper High Bay | RFQ |  | Racks | 162.5-1.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | Yes | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 7 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-070 | 121.03 | 121.03.04 | LLRF | HBB | HBB-Upper High Bay | Buncher |  | Racks | 162.5-1.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | Yes | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 15 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-071 | 121.03 | 121.03.04 | LLRF | HBB | HBB-Upper High Bay | HWR |  | Racks | 162.5-1.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | Yes | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 20 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-072 | 121.03 | 121.03.04 | LLRF | HBB | HBB-Upper High Bay | HWR |  | Racks | 162.5-1.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | Yes | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 20 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-073 | 121.03 | 121.03.04 | LLRF | HBB | HBB-Upper High Bay | RF Interlocks |  | Racks | 162.5-1.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | Yes | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 5 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-074 | 121.03 | 121.03.04 | LLRF | HBB | HBB-Upper High Bay | RF Interlocks |  | Racks | 162.5-1.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | Yes | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 71 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-075 | 121.03 | 121.03.04 | LLRF | HBB | HBB-Upper High Bay | RFQ, Buncher, HWR | Combination of all 6 racks for RFQ/Buncher/HWR. Captured here for floor space a positioning purposes. | Racks | 162.5 Station 1 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [14 empty] | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-076 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR1 | SSR1 |  | Resonance Control | MO/PRL - 4x4x1 MO+ 36U rack |  | 1 | Final | Prototype-Testing | 30% | Floor, Suspended | 84 | 48 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0.4 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0.42 | 100 | 0.42 | .4/120 | 0.4 | [5 empty] | Other | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 16 | Yes | N/A | N/A | ACNET | Wall Mounted Tunnel side @ beginning of frequecy section | C_LLRF
DN-077 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR1 | SSR1 |  | Racks | 325-1.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-078 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR1 | SSR1 |  | Racks | 325-1.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 27 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-079 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR1 | SSR1 |  | Racks | 325-1.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-080 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR1 | RF Interlocks |  | Racks | 325-1.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-081 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR1 | RF Interlocks |  | Racks | 325-1.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 87 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-082 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR1 | Spare |  | Racks | 325-1.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 112 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-083 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | SSR1 | Combination of all 6 racks for SSR station 1. Captured here for floor space a positioning purposes. | Racks | 325 Station 1 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-084 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-2.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-085 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-2.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 27 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-086 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-2.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-087 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | RF Interlocks |  | Racks | 325-2.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 154 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-088 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | RF Interlocks |  | Racks | 325-2.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-089 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | Spare |  | Racks | 325-2.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-090 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | SSR2 | Combination of all 6 racks for SSR station 2. Captured here for floor space a positioning purposes. | Racks | 325 Station 2 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-091 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-3.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-092 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-3.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 27 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-093 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-3.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-094 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | RF Interlocks |  | Racks | 325-3.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 157 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-095 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | RF Interlocks |  | Racks | 325-3.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-096 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | Spare |  | Racks | 325-3.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-097 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | SSR2 | Combination of all 6 racks for SSR station 3. Captured here for floor space a positioning purposes. | Racks | 325 Station 3 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-098 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-4.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-099 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-4.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 27 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-100 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | SSR2 |  | Racks | 325-4.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 18 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-101 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | RF Interlocks |  | Racks | 325-4.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 138 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-102 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | RF Interlocks |  | Racks | 325-4.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-103 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | Spare |  | Racks | 325-4.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-104 | 121.03 | 121.03.04 | LLRF | LG | LG-SSR2 | SSR2 | Combination of all 6 racks for SSR station 4. Captured here for floor space a positioning purposes. | Racks | 325 Station 4 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-105 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | LB650 |  | Resonance Control | MO/PRL - 4x4x1 MO+ 36U rack |  | 1 | Final | Prototype-Testing | 30% | Floor, Suspended | 84 | 48 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0.4 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0.42 | 100 | 0.42 | .4/120 | 0.4 | [5 empty] | Other | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 16 | Yes | N/A | N/A | ACNET | Wall Mounted Tunnel side @ beginning of frequecy section | C_LLRF
DN-106 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-1.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 20 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-107 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-1.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 22 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-108 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-1.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 23 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-109 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | RF Interlocks |  | Racks | 650-1.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 153 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-110 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | RF Interlocks |  | Racks | 650-1.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-111 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | Spare |  | Racks | 650-1.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-112 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | LB650 | Combination of all 6 racks for 650 station 1. Captured here for floor space a positioning purposes. | Racks | 650 Station 1 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-113 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-2.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-114 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-2.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 26 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-115 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-2.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-116 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | RF Interlocks |  | Racks | 650-2.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 154 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-117 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | RF Interlocks |  | Racks | 650-2.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-118 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | Spare |  | Racks | 650-2.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-119 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | LB650 | Combination of all 6 racks for 650 station 2. Captured here for floor space a positioning purposes. | Racks | 650 Station 2 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-120 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-3.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-121 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-3.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-122 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | LB650 |  | Racks | 650-3.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 6 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-123 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | RF Interlocks |  | Racks | 650-3.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 116 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-124 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | RF Interlocks |  | Racks | 650-3.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-125 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | Spare |  | Racks | 650-3.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-126 | 121.03 | 121.03.04 | LLRF | LG | LG-LB650 | LB650 | Combination of all 6 racks for 650 station 3. Captured here for floor space a positioning purposes. | Racks | 650 Station 3 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO, Need 3ft on all sides for access. | C_LLRF
DN-127 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | HB650 |  | Racks | 650-4.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-128 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | HB650 |  | Racks | 650-4.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 26 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-129 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | HB650 |  | Racks | 650-4.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-130 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | RF Interlocks |  | Racks | 650-4.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 144 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-131 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | RF Interlocks |  | Racks | 650-4.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-132 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | Spare |  | Racks | 650-4.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-133 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | HB650 | Combination of all 6 racks for 650 station 4. Captured here for floor space a positioning purposes. | Racks | 650 Station 4 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO | C_LLRF
DN-134 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | HB650 |  | Racks | 650-5.1 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Left Only | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-135 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | HB650 |  | Racks | 650-5.2 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 26 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-136 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | HB650 |  | Racks | 650-5.3 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 24 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-137 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | RF Interlocks |  | Racks | 650-5.4 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 144 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-138 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | RF Interlocks |  | Racks | 650-5.5 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Open | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-139 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | Spare |  | Racks | 650-5.6 |  | 0 | Final | Off the Shelf | 15% | Floor | 24 | 30 | 96 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0 | 90 | 0 | .4/120 | 0.4 | 20 | TBD | No | No | TBD | 19"W/52U X 29" D | Open | Right Only | Doors | Yes | Rigid (e.g. hardline coax) | 0 | Yes | N/A | N/A | ACNET |  | C_LLRF
DN-140 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | HB650 | Combination of all 6 racks for 650 station 5. Captured here for floor space a positioning purposes. | Racks | 650 Station 5 |  | 6 | Final | Prototype-Testing | 30% | Floor | 144 | 30 | 96 | [10 empty] | Air, Environment | 0.4 | 2.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 2.52 | 90 | 2.268 | [5 empty] | No | TBD |  | Open | Left AND Right |  | Yes | Rigid (e.g. hardline coax) |  | Yes | N/A | N/A | ACNET | Gallery location and proximity to MO. Need 3ft on all sides for access. | C_LLRF
DN-141 | 121.03 | 121.03.04 | LLRF | LG | LG-HB650 | HB650 |  | Resonance Control | 650 MO amp - 36U rack |  | 1 | Final | Prototype-Testing | 30% | Floor | 60 | 66 | 48 |  |  | Yes |  | 72+/-5 | 72+/-5 |  |  |  | 10 | Air, Environment | 0.4 | 0.4 | 1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 3.5 | 420 | 0.42 | 100 | 0.42 | [7 empty] | Other | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) | 16 | Yes | N/A | N/A | ACNET | End of frequency section | C_LLRF
DN-142 | 121.03 | 121.03.05 | Magnets | LG | LG-HWR | Magnets, Dipole Corrector , Solenoids |  | Racks | switchers, 4QPM, bulk |  | 3 | Final | Off the Shelf | 15% | Floor | 32 | 24 | 96 |  |  | No |  | 78 +/-5 | 78 +/-5 | 55 |  |  | 900 | Air, Environment | 4.5 | 13.5 | 0.8 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 208 | 32 | 11528.5302 | 34.5856 | 86 | 29.7436 | yes | [6 empty] | * 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 82 | Yes | No | Yes | Ethernet | 208/120 modification (UPS as well) | C_Magnets
DN-143 | 121.03 | 121.03.05 | Magnets | LG | LG-HWR | Solenoids |  | Power Supplies |  |  | 8 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 0.5 | [7 empty] | 0 | 0 | 86 | 0 | na | 2.4 | 20 | Yes | Yes | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 32 | No | No | Yes |  |  | C_Magnets
DN-144 | 121.03 | 121.03.05 | Magnets | LG | LG-HWR | Magnets, Dipole Corrector |  | Power Supplies |  |  | 16 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 0.04 | [7 empty] | 0 | 0 | 86 | 0 | na | 2.4 | 20 | Yes | Yes | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 50 | No | No | Yes |  |  | C_Magnets
DN-145 | 121.03 | 121.03.05 | Magnets | LT | LT-HWR | Solenoids |  | Element/magnet |  |  | 8 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 0.5 | [7 empty] | 0 | 0 | 100 | 0 | [13 empty] | 16 | No |  |  |  |  | C_Magnets
DN-146 | 121.03 | 121.03.05 | Magnets | LT | LT-HWR | Magnets, Dipole Corrector |  | Element/magnet |  |  | 16 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 0.8 | [7 empty] | 0 | 0 | 100 | 0 | [13 empty] | 32 | No |  |  |  |  | C_Magnets
DN-147 | 121.03 | 121.03.05 | Magnets | LG | LG-SSR1 | Magnets, Dipole Corrector , Solenoids |  | Racks | switchers, 8QPM, bulk |  | 6 | Final | Off the Shelf | 5% | Floor | 32 | 24 | 96 |  |  | No |  | 78 +/-5 | 78 +/-5 | 55 |  |  | 900 | Air, Environment | 1.62 | 9.72 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 208 | 32 | 11528.5302 | 69.1712 | 86 | 59.4872 | yes | [6 empty] | * 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 148 | Yes | No | Yes | Ethernet | 208/120 modification (UPS as well) | C_Magnets
DN-148 | 121.03 | 121.03.05 | Magnets | LG | LG-SSR1 | Solenoids |  | Power Supplies |  |  | 8 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 0.5 | [7 empty] | 0 | 0 | 86 | 0 | na | 2.4 | 20 | Yes | Yes | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 42 | No | No | Yes |  |  | C_Magnets
DN-149 | 121.03 | 121.03.05 | Magnets | LG | LG-SSR1 | Magnets, Dipole Corrector |  | Power Supplies |  |  | 32 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 6.6 | [7 empty] | 0 | 0 | 86 | 0 | na | 2.4 | 20 | Yes | Yes | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 106 | No | No | Yes |  |  | C_Magnets
DN-150 | 121.03 | 121.03.05 | Magnets | LT | LT-SSR1 | Solenoids |  | Magnets |  |  | 8 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 0.5 | [7 empty] | 0 | 0 |  | 0 | [13 empty] | 16 | No |  |  |  |  | C_Magnets
DN-151 | 121.03 | 121.03.05 | Magnets | LT | LT-SSR1 | Magnets, Dipole Corrector |  | Magnets |  |  | 32 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 1.6 | [7 empty] | 0 | 0 |  | 0 | [13 empty] | 64 | No |  |  |  |  | C_Magnets
DN-152 | 121.03 | 121.03.05 | Magnets | LG | LG-SSR2 | Magnets, Dipole Corrector , Solenoids |  | Racks | 208/120 rack |  | 21 | Final | Off the Shelf | 5% | Floor | 32 | 24 | 96 |  |  | No |  | 78 +/-5 | 78 +/-5 | 55 |  |  | 900 | Air, Environment | 1.5 | 31.5 | 18 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 208 | 32 | 11528.5302 | 242.0991 | 86 | 208.2053 | yes | [6 empty] | * 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 392 | Yes | No | Yes | Ethernet | 208/120 modification (UPS as well) | C_Magnets
DN-153 | 121.03 | 121.03.05 | Magnets | LG | LG-SSR2 | Solenoids |  | Power Supplies |  |  | 21 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 1.5 | [7 empty] | 0 | 0 | 86 | 0 | na | 2.4 | 20 | Yes | Yes | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 112 | No | No | Yes |  |  | C_Magnets
DN-154 | 121.03 | 121.03.05 | Magnets | LG | LG-SSR2 | Magnets, Dipole Corrector |  | Power Supplies |  |  | 84 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 4.2 | [7 empty] | 0 | 0 | 86 | 0 | na | 2.4 | 20 | Yes | Yes | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 280 | No | No | Yes |  |  | C_Magnets
DN-155 | 121.03 | 121.03.05 | Magnets | LT | LT-SSR2 | Solenoids |  | Magnets |  |  | 21 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 1.5 | [7 empty] | 0 | 0 |  | 0 | [13 empty] | 42 | No |  |  |  |  | C_Magnets
DN-156 | 121.03 | 121.03.05 | Magnets | LT | LT-SSR2 | Magnets, Dipole Corrector |  | Magnets |  |  | 84 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 22.2 | [7 empty] | 0 | 0 |  | 0 | [13 empty] | 168 | No |  |  |  |  | C_Magnets
DN-157 | 121.03 | 121.03.05 | Magnets | LG | LG-LB650, LG-HB650 | Magnets, Regular Quadrupole |  | Racks | 1.5kW supplies, 84% efficient, 8/RR + Controller/regulators |  | 5 | Final | Off the Shelf | 15% | Floor | 32 | 24 | 96 |  |  | No |  | 78 +/-5 | 78 +/-5 | 55 |  |  | 900 | Air, Environment | 5.7 | 28.5 | [5 empty] | 480Y/277 V - 3 Phase - 4 Wire | 480 | 65.4 | 54372.539 | 271.8627 | 86 | 233.8019 | [7 empty] | * 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 143 | Yes | No | Yes | Ethernet |  | C_Magnets
DN-158 | 121.03 | 121.03.05 | Magnets | LG | LG-LB650, LG-HB650 | Magnets, Regular Quadrupole |  | Power Supplies |  |  | 40 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 3.5 | [7 empty] | 0 | 0 | 84 | 0 | NA | NA | 15 | TBD | TBD | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 143 | No | No | Yes | Ethernet | 208 circuit at 27.4 amp & 110 circuit at 38 amps | C_Magnets
DN-159 | 121.03 | 121.03.05 | Magnets | LG | LG-LB650, LG-HB650 | Magnets, Dipole Corrector |  | Racks | switchers,bulk |  | 2 | Final | Off the Shelf | 15% | Floor | 32 | 24 | 96 |  |  | No |  | 78 +/-5 | 78 +/-5 | 55 |  |  | 900 | Air, Environment | 1.2 | 2.4 | [5 empty] | 480Y/277 V - 3 Phase - 4 Wire | 480 | 28.34 | 23561.4335 | 47.1229 | 86 | 40.5257 |  |  | 40 |  |  |  |  | * 19"W/52U X 29" D | Open | Left AND Right | Door | Yes | Flexible <1cm (e.g. RG58) | 83 | Yes | No | Yes | Ethernet |  | C_Magnets
DN-160 | 121.03 | 121.03.05 | Magnets | LG | LG-LB650, LG-HB650 | Magnets, Dipole Corrector |  | Power Supplies |  |  | 36 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 | [5 empty] | 0 | 0.04 | [7 empty] | 0 | 0 | 86 | 0 | NA | NA |  | TBD | TBD | No | No | In racks |  |  |  | Yes | Flexible <1cm (e.g. RG58) | 80 | No | No | Yes | Ethernet | 208 circuit at 27.4 amp & 110 circuit at 38 amps | C_Magnets
DN-161 | 121.03 | 121.03.05 | Magnets | LT | LT-LB650, LT-HB650 | Magnets, Regular Quadrupole |  | Magnets |  |  | 40 | Final | Off the Shelf | 15% | [8 empty] | 78 +/-5 | 78 +/-5 | 55 |  |  |  | LCW | 0.5 | 20 | 3.5 | [7 empty] | 0 | 0 | 100 | 0 | [13 empty] | 88 | No |  |  |  |  | C_Magnets
DN-162 | 121.03 | 121.03.05 | Magnets | LT | LT-LB650, LT-HB650 | Magnets, Dipole Corrector |  | Magnets |  |  | 36 | Final | Off the Shelf | 15% |  | 118 | [6 empty] | 78 +/-5 | 78 +/-5 | 55 |  |  |  | Air, Environment | 0.04 | 1.44 | 0.4 | [7 empty] | 0 | 0 | 100 | 0 | [13 empty] | 80 | No |  |  |  |  | C_Magnets
DN-163 | 121.03 | 121.03.08 | SS | HBB | HBB-Control Room | Interlocks |  | Racks | CDC RMSS |  | 1 | Final | Off the Shelf | 15% | Floor | 30 | 32 | 96 |  |  | No |  | 72 +/- 5 | 72 +/- 5 | 55 |  |  |  | Air, Environment | 3.6 | 3.6 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 7 | 840 | 0.84 | 100 | 0.84 | internal (provided by SS) |  | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Closed | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) |  | Yes | No | No | Ethernet | Must have an end rack 8" x 30" | C_SS
DN-164 | 121.03 | 121.03.08 | SS | LG | LG-SSR2, LG-LB650 | ODH |  | Racks | ODH |  | 1 | Final | Off the Shelf | 15% | Floor | 30 | 32 | 96 |  |  | No |  | 72 +/- 5 | 72 +/- 5 | 55 |  |  |  | Air, Environment | 2 | 2 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 7 | 840 | 0.84 | 100 | 0.84 | internal (provided by SS) |  | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Open | Yes | Flexible <1cm (e.g. RG58) |  | Yes | No | No | Ethernet | Must have an end rack 8" x 30" | C_SS
DN-165 | 121.03 | 121.03.08 | SS | LG | LG-HB650 | Interlocks |  | Racks | CDC RMSS |  | 1 | Final | Off the Shelf | 15% | Floor | 30 | 32 | 96 |  |  | No |  | 72 +/- 5 | 72 +/- 5 | 55 |  |  |  | Air, Environment | 3.6 | 3.6 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 7 | 840 | 0.84 | 100 | 0.84 | internal (provided by SS) |  | 20 | No | No | No | No | 19"W/52U X 29" D | Open | Left AND Right | Open | Yes | Semi-rigid >1cm (e.g. 0.5" Heliax) |  | Yes | No | No | Ethernet | Must have an end rack 8" x 30" | C_SS
DN-166 | 121.03 | 121.03.08 | SS | LG | LG-General | Interlocks, SSIU |  | Rack Mount | 2U rack mount |  | 22 | Final | Off the Shelf | 15% | Rack Mounted | 20 | 19 | 3 |  |  | No |  | 72 +/- 5 | 72 +/- 5 | 55 |  |  |  | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3 | 360 | 7.92 | 100 | 7.92 |  |  |  | No | No | No | No | Other |  |  |  |  | Flexible <1cm (e.g. RG58) |  | Yes | No | No | Ethernet | These SSIU units will just share rack space in other racks. | C_SS
DN-167 | 121.03 | 121.03.08 | SS | LG | LG-SSR1 | Interlocks |  | Interlock Box | Wall Mounted |  | 1 | Final | Off the Shelf | 5% | Suspended | 30 | 8 | 20 | [10 empty] | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3 | 360 | 0.36 | 100 | 0.36 | [14 empty] | Yes |  |  |  |  | C_SS
DN-168 | 121.03 | 121.03.08 | SS | LG | LG-BTL | Interlocks |  | Interlock Box | Wall Mounted |  | 1 | Final | Off the Shelf | 5% | Suspended | 30 | 8 | 20 | [10 empty] | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 3 | 360 | 0.36 | 100 | 0.36 | [14 empty] | Yes |  |  |  |  | C_SS
DN-169 | 121.03 | 121.03.06 | Vacuum | LT | LT-HWR | HWR |  | Gauges, Ion | SRF Warm units | 4 | 2 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-170 | 121.03 | 121.03.06 | Vacuum | LT | LT-HWR | HWR |  | Gauges, Pirani | SRF Warm units |  | 2 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-171 | 121.03 | 121.03.06 | Vacuum | LT | LT-HWR | HWR |  | Pump, Ion | SRF Warm units |  | 1 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.1 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-172 | 121.03 | 121.03.06 | Vacuum | LT | LT-HWR | HWR |  | Pump, Roughing | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 208 V - 1 Phase - 2 Wire | 208 | 5 | 1040 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | Yes |  |  |  |  | C_Vacuum
DN-173 | 121.03 | 121.03.06 | Vacuum | LT | LT-HWR | HWR |  | Pump, Turbo | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 72 | Yes |  |  |  |  | C_Vacuum
DN-174 | 121.03 | 121.03.06 | Vacuum | LT | LT-HWR | HWR |  | Valves, Right Angle | SRF Warm units |  | 2 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.072 | 100 | 0.072 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-175 | 121.03 | 121.03.06 | Vacuum | LG | LG-HWR | HWR |  | Controller, Ion Pump | SRF Warm units |  | 1 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.1 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.014549 | 100 | 0.014549 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-176 | 121.03 | 121.03.06 | Vacuum | LG | LG-HWR | HWR |  | Controller, Turbo Pump | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [6 empty] | 120 | 0.5 | 103.923 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-177 | 121.03 | 121.03.06 | Vacuum | LG | LG-HWR | HWR |  | Controller, Ion/Pirani Gauge | SRF Warm units |  | 1 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.1 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.06 | 100 | 0.06 | [12 empty] | Flexible <1cm (e.g. RG58) | 40 | Yes |  |  |  |  | C_Vacuum
DN-178 | 121.03 | 121.03.06 | Vacuum | LG | LG-HWR | HWR |  | Racks | SRF Warm units |  | 1 | Final | Off the Shelf | 5% | Floor | [15 empty] | 0 | [8 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-179 | 121.03 | 121.03.06 | Vacuum | LT | LT-HWR | HWR |  | Gauges, Ion | Insulating Vacuum | 2 | 1 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.1 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-180 | 121.03 | 121.03.06 | Vacuum | LT | LT-HWR | HWR |  | Gauges, Pirani | Insulating Vacuum | 2 | 1 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.1 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-181 | 121.03 | 121.03.06 | Vacuum | LT | LT-HWR | HWR |  | Pump, Ion | Insulating Vacuum | 1 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-182 | 121.03 | 121.03.06 | Vacuum | LT | LT-HWR | HWR |  | Pump, Roughing | Insulating Vacuum | 0 | 1 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 208 V - 1 Phase - 2 Wire | 208 | 5 | 1040 | 1.04 | 100 | 1.04 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | Yes |  |  |  |  | C_Vacuum
DN-183 | 121.03 | 121.03.06 | Vacuum | LT | LT-HWR | HWR |  | Pump, Turbo | Insulating Vacuum | 0 | 1 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 0.48 | 100 | 0.48 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 72 | Yes |  |  |  |  | C_Vacuum
DN-184 | 121.03 | 121.03.06 | Vacuum | LT | LT-HWR | HWR |  | Valves, Right Angle | Insulating Vacuum | 2 | 3 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.108 | 100 | 0.108 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-185 | 121.03 | 121.03.06 | Vacuum | LG | LG-HWR | HWR |  | Controller, Ion Pump | Insulating Vacuum | 1 | 0 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-186 | 121.03 | 121.03.06 | Vacuum | LG | LG-HWR | HWR |  | Controller, Turbo Pump | Insulating Vacuum | 0 | 1 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [6 empty] | 120 | 0.5 | 103.923 | 0.10392 | 100 | 0.10392 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-187 | 121.03 | 121.03.06 | Vacuum | LG | LG-HWR | HWR |  | Controller, Ion/Pirani Gauge | Insulating Vacuum | 1 | 1 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.1 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.06 | 100 | 0.06 | [12 empty] | Flexible <1cm (e.g. RG58) | 40 | Yes |  |  |  |  | C_Vacuum
DN-188 | 121.03 | 121.03.06 | Vacuum | LG | LG-HWR | HWR |  | Racks | Insulating Vacuum |  | 1 | Final | Off the Shelf | 5% | Floor | [15 empty] | 0 | [8 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-189 | 121.03 | 121.03.06 | Vacuum | LT | LT-SSR1 | SSR1 |  | Gauges, Ion | SRF Warm units |  | 4 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-190 | 121.03 | 121.03.06 | Vacuum | LT | LT-SSR1 | SSR1 |  | Gauges, Pirani | SRF Warm units |  | 4 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-191 | 121.03 | 121.03.06 | Vacuum | LT | LT-SSR1 | SSR1 |  | Pump, Ion | SRF Warm units |  | 2 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-192 | 121.03 | 121.03.06 | Vacuum | LT | LT-SSR1 | SSR1 |  | Pump, Roughing | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 208 V - 1 Phase - 2 Wire | 208 | 5 | 1040 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | Yes |  |  |  |  | C_Vacuum
DN-193 | 121.03 | 121.03.06 | Vacuum | LT | LT-SSR1 | SSR1 |  | Pump, Turbo | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 72 | Yes |  |  |  |  | C_Vacuum
DN-194 | 121.03 | 121.03.06 | Vacuum | LT | LT-SSR1 | SSR1 |  | Valves, Right Angle | SRF Warm units |  | 4 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.144 | 100 | 0.144 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-195 | 121.03 | 121.03.06 | Vacuum | LG | LG-SSR1 | SSR1 |  | Controller, Ion Pump | SRF Warm units |  | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.029098 | 100 | 0.029098 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-196 | 121.03 | 121.03.06 | Vacuum | LG | LG-SSR1 | SSR1 |  | Controller, Turbo Pump | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [6 empty] | 120 | 0.5 | 103.923 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-197 | 121.03 | 121.03.06 | Vacuum | LG | LG-SSR1 | SSR1 |  | Controller, Ion/Pirani Gauge | SRF Warm units |  | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.12 | 100 | 0.12 | [12 empty] | Flexible <1cm (e.g. RG58) | 40 | Yes |  |  |  |  | C_Vacuum
DN-198 | 121.03 | 121.03.06 | Vacuum | LG | LG-SSR1 | SSR1 |  | Racks | SRF Warm units |  | 1 | Final | Off the Shelf | 5% | Floor | [15 empty] | 0 | [8 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-199 | 121.03 | 121.03.06 | Vacuum | LT | LT-SSR1 | SSR1 |  | Gauges, Ion | Insulating Vacuum | 2 | 4 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-200 | 121.03 | 121.03.06 | Vacuum | LT | LT-SSR1 | SSR1 |  | Gauges, Pirani | Insulating Vacuum | 2 | 4 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-201 | 121.03 | 121.03.06 | Vacuum | LT | LT-SSR1 | SSR1 |  | Pump, Ion | Insulating Vacuum | 1 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-202 | 121.03 | 121.03.06 | Vacuum | LT | LT-SSR1 | SSR1 |  | Pump, Roughing | Insulating Vacuum | 0 | 2 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 1 | 0.5 |  |  |  |  | 208 V - 1 Phase - 2 Wire | 208 | 5 | 1040 | 2.08 | 100 | 2.08 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | Yes |  |  |  |  | C_Vacuum
DN-203 | 121.03 | 121.03.06 | Vacuum | LT | LT-SSR1 | SSR1 |  | Pump, Turbo | Insulating Vacuum | 0 | 2 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 1 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 0.96 | 100 | 0.96 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 72 | Yes |  |  |  |  | C_Vacuum
DN-204 | 121.03 | 121.03.06 | Vacuum | LT | LT-SSR1 | SSR1 |  | Valves, Right Angle | Insulating Vacuum | 2 | 6 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.216 | 100 | 0.216 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-205 | 121.03 | 121.03.06 | Vacuum | LG | LG-SSR1 | SSR1 |  | Controller, Ion Pump | Insulating Vacuum | 1 | 0 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-206 | 121.03 | 121.03.06 | Vacuum | LG | LG-SSR1 | SSR1 |  | Controller, Turbo Pump | Insulating Vacuum | 0 | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [6 empty] | 120 | 0.5 | 103.923 | 0.20785 | 100 | 0.20785 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-207 | 121.03 | 121.03.06 | Vacuum | LG | LG-SSR1 | SSR1 |  | Controller, Ion/Pirani Gauge | Insulating Vacuum | 1 | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.12 | 100 | 0.12 | [12 empty] | Flexible <1cm (e.g. RG58) | 40 | Yes |  |  |  |  | C_Vacuum
DN-208 | 121.03 | 121.03.06 | Vacuum | LG | LG-SSR1 | SSR1 |  | Racks | Insulating Vacuum |  | 1 | Final | Off the Shelf | 5% | Floor | [15 empty] | 0 | [8 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-209 | 121.3 | 121.03.06 | Vacuum | LT | LT-SSR2 | SSR2 |  | Gauges, Ion | SRF Warm units |  | 14 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 1.4 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-210 | 121.3 | 121.03.06 | Vacuum | LT | LT-SSR2 | SSR2 |  | Gauges, Pirani | SRF Warm units |  | 14 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 1.4 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-211 | 121.3 | 121.03.06 | Vacuum | LT | LT-SSR2 | SSR2 |  | Pump, Ion | SRF Warm units |  | 7 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.7 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-212 | 121.3 | 121.03.06 | Vacuum | LT | LT-SSR2 | SSR2 |  | Pump, Roughing | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 208 V - 1 Phase - 2 Wire | 208 | 5 | 1040 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | Yes |  |  |  |  | C_Vacuum
DN-213 | 121.3 | 121.03.06 | Vacuum | LT | LT-SSR2 | SSR2 |  | Pump, Turbo | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 72 | Yes |  |  |  |  | C_Vacuum
DN-214 | 121.3 | 121.03.06 | Vacuum | LT | LT-SSR2 | SSR2 |  | Valves, Right Angle | SRF Warm units |  | 14 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.504 | 100 | 0.504 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-215 | 121.3 | 121.03.06 | Vacuum | LG | LT-SSR2 | SSR2 |  | Controller, Ion Pump | SRF Warm units |  | 7 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.7 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.10184 | 100 | 0.10184 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-216 | 121.3 | 121.03.06 | Vacuum | LG | LT-SSR2 | SSR2 |  | Controller, Turbo Pump | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [6 empty] | 120 | 0.5 | 103.923 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-217 | 121.3 | 121.03.06 | Vacuum | LG | LT-SSR2 | SSR2 |  | Controller, Ion/Pirani Gauge | SRF Warm units |  | 14 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 1.4 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.84 | 100 | 0.84 | [12 empty] | Flexible <1cm (e.g. RG58) | 40 | Yes |  |  |  |  | C_Vacuum
DN-218 | 121.3 | 121.03.06 | Vacuum | LG | LT-SSR2 | SSR2 |  | Racks | SRF Warm units |  | 1 | Final | Off the Shelf | 5% | Floor | [15 empty] | 0 | [8 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-219 | 121.3 | 121.03.06 | Vacuum | LT | LT-SSR2 | SSR2 |  | Gauges, Ion | Insulating Vacuum | 2 | 14 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 1.4 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-220 | 121.3 | 121.03.06 | Vacuum | LT | LT-SSR2 | SSR2 |  | Gauges, Pirani | Insulating Vacuum | 2 | 14 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 1.4 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-221 | 121.3 | 121.03.06 | Vacuum | LT | LT-SSR2 | SSR2 |  | Pump, Ion | Insulating Vacuum | 1 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-222 | 121.3 | 121.03.06 | Vacuum | LT | LT-SSR2 | SSR2 |  | Pump, Roughing | Insulating Vacuum | 0 | 7 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 3.5 | 0.5 |  |  |  |  | 208 V - 1 Phase - 2 Wire | 208 | 5 | 1040 | 7.28 | 100 | 7.28 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | Yes |  |  |  |  | C_Vacuum
DN-223 | 121.3 | 121.03.06 | Vacuum | LT | LT-SSR2 | SSR2 |  | Pump, Turbo | Insulating Vacuum | 0 | 7 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 3.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 3.36 | 100 | 3.36 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 72 | Yes |  |  |  |  | C_Vacuum
DN-224 | 121.3 | 121.03.06 | Vacuum | LT | LT-SSR2 | SSR2 |  | Valves, Right Angle | Insulating Vacuum | 2 | 21 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.756 | 100 | 0.756 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-225 | 121.3 | 121.03.06 | Vacuum | LG | LG-SSR2 | SSR2 |  | Controller, Ion Pump | Insulating Vacuum | 1 | 0 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-226 | 121.3 | 121.03.06 | Vacuum | LG | LG-SSR2 | SSR2 |  | Controller, Turbo Pump | Insulating Vacuum | 0 | 7 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [6 empty] | 120 | 0.5 | 103.923 | 0.72746 | 100 | 0.72746 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-227 | 121.3 | 121.03.06 | Vacuum | LG | LG-SSR2 | SSR2 |  | Controller, Ion/Pirani Gauge | Insulating Vacuum | 1 | 7 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.7 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.42 | 100 | 0.42 | [12 empty] | Flexible <1cm (e.g. RG58) | 40 | Yes |  |  |  |  | C_Vacuum
DN-228 | 121.3 | 121.03.06 | Vacuum | LG | LG-SSR2 | SSR2 |  | Racks | Insulating Vacuum |  | 1 | Final | Off the Shelf | 5% | Floor | [15 empty] | 0 | [8 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-229 | 121.3 | 121.03.06 | Vacuum | LT | LT-LB650 | LB650 |  | Gauges, Ion | SRF Warm units |  | 18 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 1.8 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-230 | 121.3 | 121.03.06 | Vacuum | LT | LT-LB650 | LB650 |  | Gauges, Pirani | SRF Warm units |  | 18 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 1.8 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-231 | 121.3 | 121.03.06 | Vacuum | LT | LT-LB650 | LB650 |  | Pump, Ion | SRF Warm units |  | 9 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.9 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-232 | 121.3 | 121.03.06 | Vacuum | LT | LT-LB650 | LB650 |  | Pump, Roughing | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 208 V - 1 Phase - 2 Wire | 208 | 5 | 1040 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | Yes |  |  |  |  | C_Vacuum
DN-233 | 121.3 | 121.03.06 | Vacuum | LT | LT-LB650 | LB650 |  | Pump, Turbo | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 72 | Yes |  |  |  |  | C_Vacuum
DN-234 | 121.3 | 121.03.06 | Vacuum | LT | LT-LB650 | LB650 |  | Valves, Right Angle | SRF Warm units |  | 18 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.648 | 100 | 0.648 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-235 | 121.3 | 121.03.06 | Vacuum | LG | LT-LB650 | LB650 |  | Controller, Ion Pump | SRF Warm units |  | 9 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.9 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.13094 | 100 | 0.13094 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-236 | 121.3 | 121.03.06 | Vacuum | LG | LT-LB650 | LB650 |  | Controller, Turbo Pump | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [6 empty] | 120 | 0.5 | 103.923 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-237 | 121.3 | 121.03.06 | Vacuum | LG | LT-LB650 | LB650 |  | Controller, Ion/Pirani Gauge | SRF Warm units |  | 9 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.9 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.54 | 100 | 0.54 | [12 empty] | Flexible <1cm (e.g. RG58) | 40 | Yes |  |  |  |  | C_Vacuum
DN-238 | 121.3 | 121.03.06 | Vacuum | LG | LT-LB650 | LB650 |  | Racks | SRF Warm units |  | 1 | Final | Off the Shelf | 5% | Floor | [15 empty] | 0 | [8 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-239 | 121.3 | 121.03.06 | Vacuum | LT | LT-LB650 | LB650 |  | Gauges, Ion | Insulating Vacuum | 2 | 18 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 1.8 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-240 | 121.3 | 121.03.06 | Vacuum | LT | LT-LB650 | LB650 |  | Gauges, Pirani | Insulating Vacuum | 2 | 18 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 1.8 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-241 | 121.3 | 121.03.06 | Vacuum | LT | LT-LB650 | LB650 |  | Pump, Ion | Insulating Vacuum | 1 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-242 | 121.3 | 121.03.06 | Vacuum | LT | LT-LB650 | LB650 |  | Pump, Roughing | Insulating Vacuum | 0 | 9 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 4.5 | 0.5 |  |  |  |  | 208 V - 1 Phase - 2 Wire | 208 | 5 | 1040 | 9.36 | 100 | 9.36 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | Yes |  |  |  |  | C_Vacuum
DN-243 | 121.3 | 121.03.06 | Vacuum | LT | LT-LB650 | LB650 |  | Pump, Turbo | Insulating Vacuum | 0 | 9 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 4.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 4.32 | 100 | 4.32 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 72 | Yes |  |  |  |  | C_Vacuum
DN-244 | 121.3 | 121.03.06 | Vacuum | LT | LT-LB650 | LB650 |  | Valves, Right Angle | Insulating Vacuum | 2 | 27 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.972 | 100 | 0.972 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-245 | 121.3 | 121.03.06 | Vacuum | LG | LG-LB650 | LB650 |  | Controller, Ion Pump | Insulating Vacuum | 1 | 0 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-246 | 121.3 | 121.03.06 | Vacuum | LG | LG-LB650 | LB650 |  | Controller, Turbo Pump | Insulating Vacuum | 0 | 9 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [6 empty] | 120 | 0.5 | 103.923 | 0.93531 | 100 | 0.93531 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-247 | 121.3 | 121.03.06 | Vacuum | LG | LG-LB650 | LB650 |  | Controller, Ion/Pirani Gauge | Insulating Vacuum | 1 | 9 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.9 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.54 | 100 | 0.54 | [12 empty] | Flexible <1cm (e.g. RG58) | 40 | Yes |  |  |  |  | C_Vacuum
DN-248 | 121.3 | 121.03.06 | Vacuum | LG | LG-LB650 | LB650 |  | Racks | Insulating Vacuum |  | 1 | Final | Off the Shelf | 5% | Floor | [15 empty] | 0 | [8 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-249 | 121.3 | 121.03.06 | Vacuum | LT | LT-HB650 | HB650 |  | Gauges, Ion | SRF Warm units |  | 8 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.8 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-250 | 121.3 | 121.03.06 | Vacuum | LT | LT-HB650 | HB650 |  | Gauges, Pirani | SRF Warm units |  | 8 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.8 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-251 | 121.3 | 121.03.06 | Vacuum | LT | LT-HB650 | HB650 |  | Pump, Ion | SRF Warm units |  | 4 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-252 | 121.3 | 121.03.06 | Vacuum | LT | LT-HB650 | HB650 |  | Pump, Roughing | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 208 V - 1 Phase - 2 Wire | 208 | 5 | 1040 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | Yes |  |  |  |  | C_Vacuum
DN-253 | 121.3 | 121.03.06 | Vacuum | LT | LT-HB650 | HB650 |  | Pump, Turbo | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 72 | Yes |  |  |  |  | C_Vacuum
DN-254 | 121.3 | 121.03.06 | Vacuum | LT | LT-HB650 | HB650 |  | Valves, Right Angle | SRF Warm units |  | 8 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.288 | 100 | 0.288 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-255 | 121.3 | 121.03.06 | Vacuum | LG | LT-HB650 | HB650 |  | Controller, Ion Pump | SRF Warm units |  | 4 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.058197 | 100 | 0.058197 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-256 | 121.3 | 121.03.06 | Vacuum | LG | LT-HB650 | HB650 |  | Controller, Turbo Pump | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [6 empty] | 120 | 0.5 | 103.923 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-257 | 121.3 | 121.03.06 | Vacuum | LG | LT-HB650 | HB650 |  | Controller, Ion/Pirani Gauge | SRF Warm units |  | 4 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.24 | 100 | 0.24 | [12 empty] | Flexible <1cm (e.g. RG58) | 40 | Yes |  |  |  |  | C_Vacuum
DN-258 | 121.3 | 121.03.06 | Vacuum | LG | LT-HB650 | HB650 |  | Racks | SRF Warm units |  | 1 | Final | Off the Shelf | 5% | Floor | [15 empty] | 0 | [8 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-259 | 121.3 | 121.03.06 | Vacuum | LT | LT-HB650 | HB650 |  | Gauges, Ion | Insulating Vacuum | 2 | 8 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.8 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-260 | 121.3 | 121.03.06 | Vacuum | LT | LT-HB650 | HB650 |  | Gauges, Pirani | Insulating Vacuum | 2 | 8 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.8 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-261 | 121.3 | 121.03.06 | Vacuum | LT | LT-HB650 | HB650 |  | Pump, Ion | Insulating Vacuum | 1 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-262 | 121.3 | 121.03.06 | Vacuum | LT | LT-HB650 | HB650 |  | Pump, Roughing | Insulating Vacuum | 0 | 4 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 2 | 0.5 |  |  |  |  | 208 V - 1 Phase - 2 Wire | 208 | 5 | 1040 | 4.16 | 100 | 4.16 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | Yes |  |  |  |  | C_Vacuum
DN-263 | 121.3 | 121.03.06 | Vacuum | LT | LT-HB650 | HB650 |  | Pump, Turbo | Insulating Vacuum | 0 | 4 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 2 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 1.92 | 100 | 1.92 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 72 | Yes |  |  |  |  | C_Vacuum
DN-264 | 121.3 | 121.03.06 | Vacuum | LT | LT-HB650 | HB650 |  | Valves, Right Angle | Insulating Vacuum | 2 | 12 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.432 | 100 | 0.432 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-265 | 121.3 | 121.03.06 | Vacuum | LG | LG-HB650 | HB650 |  | Controller, Ion Pump | Insulating Vacuum | 1 | 0 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-266 | 121.3 | 121.03.06 | Vacuum | LG | LG-HB650 | HB650 |  | Controller, Turbo Pump | Insulating Vacuum | 0 | 4 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [6 empty] | 120 | 0.5 | 103.923 | 0.41569 | 100 | 0.41569 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-267 | 121.3 | 121.03.06 | Vacuum | LG | LG-HB650 | HB650 |  | Controller, Ion/Pirani Gauge | Insulating Vacuum | 1 | 4 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.24 | 100 | 0.24 | [12 empty] | Flexible <1cm (e.g. RG58) | 40 | Yes |  |  |  |  | C_Vacuum
DN-268 | 121.3 | 121.03.06 | Vacuum | LG | LG-HB650 | HB650 |  | Racks | Insulating Vacuum |  | 1 | Final | Off the Shelf | 5% | Floor | [15 empty] | 0 | [8 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-269 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | HB650 |  | Gauges, Ion | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-270 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | HB650 |  | Gauges, Pirani | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-271 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | HB650 |  | Pump, Ion | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-272 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | HB650 |  | Pump, Roughing | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 208 V - 1 Phase - 2 Wire | 208 | 5 | 1040 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | Yes |  |  |  |  | C_Vacuum
DN-273 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | HB650 |  | Pump, Turbo | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 72 | Yes |  |  |  |  | C_Vacuum
DN-274 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | HB650 |  | Valves, Right Angle | SRF Warm units |  | 4 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.144 | 100 | 0.144 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-275 | 121.3 | 121.03.06 | Vacuum | LT | LG-Upgrade | HB650 |  | Controller, Ion Pump | SRF Warm units |  | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.029098 | 100 | 0.029098 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-276 | 121.3 | 121.03.06 | Vacuum | LG | LG-Upgrade | HB650 |  | Controller, Turbo Pump | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [6 empty] | 120 | 0.5 | 103.923 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-277 | 121.3 | 121.03.06 | Vacuum | LG | LG-Upgrade | HB650 |  | Controller, Ion/Pirani Gauge | SRF Warm units |  | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.12 | 100 | 0.12 | [12 empty] | Flexible <1cm (e.g. RG58) | 40 | Yes |  |  |  |  | C_Vacuum
DN-278 | 121.3 | 121.03.06 | Vacuum | LG | LG-Upgrade | HB650 |  | Racks | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Floor | [15 empty] | 0 | [8 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-279 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | HB650 |  | Gauges, Ion | Insulating Vacuum | 2 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-280 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | HB650 |  | Gauges, Pirani | Insulating Vacuum | 2 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-281 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | HB650 |  | Pump, Ion | Insulating Vacuum | 1 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-282 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | HB650 |  | Pump, Roughing | Insulating Vacuum | 0 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 208 V - 1 Phase - 2 Wire | 208 | 5 | 1040 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | Yes |  |  |  |  | C_Vacuum
DN-283 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | HB650 |  | Pump, Turbo | Insulating Vacuum | 0 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 72 | Yes |  |  |  |  | C_Vacuum
DN-284 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | HB650 |  | Valves, Right Angle | Insulating Vacuum | 2 | 6 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.216 | 100 | 0.216 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-285 | 121.3 | 121.03.06 | Vacuum | LG | LG-Upgrade | HB650 |  | Controller, Ion Pump | Insulating Vacuum | 1 | 0 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-286 | 121.3 | 121.03.06 | Vacuum | LG | LG-Upgrade | HB650 |  | Controller, Turbo Pump | Insulating Vacuum | 0 | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [6 empty] | 120 | 0.5 | 103.923 | 0.20785 | 100 | 0.20785 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-287 | 121.3 | 121.03.06 | Vacuum | LG | LG-Upgrade | HB650 |  | Controller, Ion/Pirani Gauge | Insulating Vacuum | 1 | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.12 | 100 | 0.12 | [12 empty] | Flexible <1cm (e.g. RG58) | 40 | Yes |  |  |  |  | C_Vacuum
DN-288 | 121.3 | 121.03.06 | Vacuum | LG | LG-Upgrade | HB650 |  | Racks | Insulating Vacuum |  | 0 | Final | Off the Shelf | 5% | Floor | [15 empty] | 0 | [8 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-289 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | RFSeparator |  | Gauges, Ion | SRF Warm units | 4 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-290 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | RFSeparator |  | Gauges, Pirani | SRF Warm units | 4 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-291 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | RFSeparator |  | Pump, Ion | SRF Warm units | 2 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 20 | No |  |  |  | powered through controller | C_Vacuum
DN-292 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | RFSeparator |  | Pump, Roughing | SRF Warm units | 2 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 208 V - 1 Phase - 2 Wire | 208 | 5 | 1040 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | Yes |  |  |  |  | C_Vacuum
DN-293 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | RFSeparator |  | Pump, Turbo | SRF Warm units | 2 | 0 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 0 | 100 | 0 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 72 | Yes |  |  |  |  | C_Vacuum
DN-294 | 121.3 | 121.03.06 | Vacuum | LT | LT-Upgrade | RFSeparator |  | Valves, Right Angle | SRF Warm units | 4 | 4 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.144 | 100 | 0.144 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-295 | 121.3 | 121.03.06 | Vacuum | LT | LG-Upgrade | RFSeparator |  | Controller, Ion Pump | SRF Warm units | 2 | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.029098 | 100 | 0.029098 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-296 | 121.3 | 121.03.06 | Vacuum | LG | LG-Upgrade | RFSeparator |  | Controller, Turbo Pump | SRF Warm units | 2 | 0 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [6 empty] | 120 | 0.5 | 103.923 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 24 | Yes |  |  |  |  | C_Vacuum
DN-297 | 121.3 | 121.03.06 | Vacuum | LG | LG-Upgrade | RFSeparator |  | Controller, Ion/Pirani Gauge | SRF Warm units | 4 | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.12 | 100 | 0.12 | [12 empty] | Flexible <1cm (e.g. RG58) | 40 | Yes |  |  |  |  | C_Vacuum
DN-298 | 121.3 | 121.03.06 | Vacuum | LG | LG-Upgrade | RFSeparator |  | Racks | SRF Warm units |  | 0 | Final | Off the Shelf | 5% | Floor | [15 empty] | 0 | [8 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-299 | 121.03 | 121.03.06 | Vacuum | LT | LT-HWR | HWR |  | Valves, Gate | Fast Acting |  | 1 | Preliminary | Prototype-Testing | 25% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.036 | 100 | 0.036 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-300 | 121.03 | 121.03.06 | Vacuum | LT | LT-HB650 | HB650 |  | Valves, Gate | Fast Acting |  | 1 | Preliminary | Prototype-Testing | 25% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 0.3 | 36 | 0.036 | 100 | 0.036 | [11 empty] | Yes | Flexible <1cm (e.g. RG58) |  | Yes |  |  |  |  | C_Vacuum
DN-301 | 121.03 | 121.03.06 | Vacuum | LT | LT-LB650, LT-HB650 | Insulating Vac |  | Valves | Check valves |  | 22 | Final | Off the Shelf | 5% | Beamline/Tunnel | [15 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [13 empty] | 24 | No |  |  |  |  | C_Vacuum
DN-302 | 121.03 | 121.03.06 | Vacuum | HBB | HBB-Upper High Bay | WFE |  | Racks | Rack Contains all Ion Pump Controllers, Turbo Pump Controlers, Gauge readbacks |  | 2 | Final | Off the Shelf | 5% | Floor | 24 | 32 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 1 | 0.5 | [7 empty] | 0 | 0 | 100 | 0 | [7 empty] | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes |  | 4 | No |  |  | Ethernet | Additional 120V 10A circuit for network switch | C_Vacuum
DN-303 | 121.03 | 121.03.06 | Vacuum | HBB | HBB-Upper High Bay | WFE |  | Power Supplies |  |  | 1 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 24 | 2.45 | 101.8446 | 0.10184 | 100 | 0.10184 | [12 empty] | Semi-rigid >1cm (e.g. 0.5" Heliax) |  | No |  |  |  | Rack Power supply (I may be doubling the load from the rack equipment) | C_Vacuum
DN-304 | 121.03 | 121.03.06 | Vacuum | HBB | HBB-Lower High Bay | WFE |  | Pump, Ion |  |  | 9 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.9 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 9 | No |  |  |  | powered through controller | C_Vacuum
DN-305 | 121.03 | 121.03.06 | Vacuum | HBB | HBB-Lower High Bay | WFE |  | NEG |  |  | 2 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 2 | No |  |  |  | powered through controller | C_Vacuum
DN-306 | 121.03 | 121.03.06 | Vacuum | HBB | HBB-Upper High Bay | WFE |  | NEG Controller |  |  | 2 | Final | Off the Shelf | 5% | Rack Mounted | [13 empty] | Air, Environment |  | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_Vacuum
DN-307 | 121.03 | 121.03.06 | Vacuum | HBB | HBB-Lower High Bay | WFE |  | Pump, Turbo |  |  | 11 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 5.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 5.28 | 100 | 5.28 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 33 | Yes |  |  |  |  | C_Vacuum
DN-308 | 121.03 | 121.03.06 | Vacuum | HBB | HBB-Upper High Bay | WFE |  | Controller, Ion Pump |  |  | 9 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.9 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.13094 | 100 | 0.13094 | [12 empty] | Flexible <1cm (e.g. RG58) | 9 | No |  |  |  |  | C_Vacuum
DN-309 | 121.03 | 121.03.06 | Vacuum | HBB | HBB-Upper High Bay | WFE |  | Controller, Turbo Pump |  |  | 11 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 1 | 120 | 1.32 | 100 | 1.32 | [12 empty] | Flexible <1cm (e.g. RG58) | 11 | Yes |  |  |  |  | C_Vacuum
DN-310 | 121.03 | 121.03.06 | Vacuum | HBB | HBB-Lower High Bay | WFE |  | Gauges, Ion |  |  | 17 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 1.7 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 17 | No |  |  |  | powered through controller | C_Vacuum
DN-311 | 121.03 | 121.03.06 | Vacuum | HBB | HBB-Lower High Bay | WFE |  | Controller, Ion/Pirani Gauge |  |  | 17 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 1.7 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 1.02 | 100 | 1.02 | [12 empty] | Flexible <1cm (e.g. RG58) | 17 | Yes |  |  |  |  | C_Vacuum
DN-312 | 121.03 | 121.03.06 | Vacuum | BAL | BAL-Beam Absorber | BTL/BAL |  | Pump, Ion |  |  | 4 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 4 | No |  |  |  | powered through controller | C_Vacuum
DN-313 | 121.03 | 121.03.06 | Vacuum | BAL Area | BAL-Beam Absorber | BTL/BAL |  | Controller, Ion Pump |  |  | 4 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.058197 | 100 | 0.058197 | [12 empty] | Flexible <1cm (e.g. RG58) | 4 | No |  |  |  |  | C_Vacuum
DN-314 | 121.03 | 121.03.06 | Vacuum | BAL | BAL-Beam Absorber | BTL/BAL |  | Pump, Turbo |  |  | 2 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 1 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 4 | 480 | 0.96 | 100 | 0.96 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) | 6 | Yes |  |  |  |  | C_Vacuum
DN-315 | 121.03 | 121.03.06 | Vacuum | BAL Area | BAL-Beam Absorber | BTL/BAL |  | Controller, Turbo Pump |  |  | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 1 | 120 | 0.24 | 100 | 0.24 | [12 empty] | Flexible <1cm (e.g. RG58) | 2 | Yes |  |  |  |  | C_Vacuum
DN-316 | 121.03 | 121.03.06 | Vacuum | BAL | BAL-Beam Absorber | BTL/BAL |  | Gauges, Ion |  |  | 4 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 4 | No |  |  |  | powered through controller | C_Vacuum
DN-317 | 121.03 | 121.03.06 | Vacuum | BAL | BAL-Beam Absorber | BTL/BAL |  | Gauges, Pirani |  |  | 2 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.2 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 2 | No |  |  |  | powered through controller | C_Vacuum
DN-318 | 121.03 | 121.03.06 | Vacuum | BAL Area | BAL-Beam Absorber | BTL/BAL |  | Controller, Ion/Pirani Gauge |  |  | 6 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.6 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.36 | 100 | 0.36 | [12 empty] | Flexible <1cm (e.g. RG58) | 6 | Yes |  |  |  |  | C_Vacuum
DN-319 | 121.03 | 121.03.06 | Vacuum | BAL Area | BAL-Beam Absorber | BTL/BAL |  | Racks |  |  | 1 | Final | Off the Shelf | 5% | Floor | 24 | 32 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 0.5 | 0.5 | [7 empty] | 0 | 0 | 100 | 0 | [7 empty] | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes |  | 2 | No |  |  | Ethernet | Additional 120V 10A circuit for network switch | C_Vacuum
DN-320 | 121.03 | 121.03.06 | Vacuum | BAL Area | BAL-Beam Absorber | BTL/BAL |  | Power Supplies |  |  | 1 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 24 | 1.4 | 58.1969 | 0.058197 | 100 | 0.058197 | [12 empty] | Semi-rigid >1cm (e.g. 0.5" Heliax) |  | No |  |  |  | Rack Power supply (I may be doubling the load from the rack equipment) | C_Vacuum
DN-321 | 121.03 | 121.03.06 | Vacuum | LG | LG-BTL | BTL/BAL |  | Racks |  |  | 2 | Final | Off the Shelf | 5% | Floor | 24 | 32 | 96 |  |  |  |  | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.5 | 1 | 0.5 | [7 empty] | 0 | 0 | 100 | 0 | [7 empty] | 19"W/52U X 29" D | Open | Left AND Right | Door | Yes |  | 4 | No |  |  | Ethernet | Additional 120V 10A circuit for network switch | C_Vacuum
DN-322 | 121.03 | 121.03.06 | Vacuum | BTL | BTL-Beamline Tunnel | BTL/BAL |  | Pump, Ion |  |  | 53 | Final | Off the Shelf | 5% | Beamline/Tunnel | 8 | [6 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 5.3 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 53 | No |  |  |  | powered through controller | C_Vacuum
DN-323 | 121.03 | 121.03.06 | Vacuum | LG | LG-BTL | BTL/BAL |  | Controller, Ion Pump |  |  | 53 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 5.3 | 0.1 |  |  |  |  | 208Y/120 V - 3 Phase - 4 Wire | 24 | 0.35 | 14.5492 | 0.77111 | 100 | 0.77111 | [12 empty] | Flexible <1cm (e.g. RG58) |  | No |  |  |  |  | C_Vacuum
DN-324 | 121.03 | 121.03.06 | Vacuum | LG | LG-BTL | BTL/BAL |  | Power Supplies |  |  | 2 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment |  | 0 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 24 | 18 | 748.2459 | 1.4965 | 100 | 1.4965 | [12 empty] | Semi rigid <1cm (e.g. 0.25" Heliax) |  | No |  |  |  | Rack Power supply (I may be doubling the load from the rack equipment) | C_Vacuum
DN-325 | 121.03 | 121.03.06 | Vacuum | BTL | BTL-Beamline Tunnel | BTL/BAL |  | Gauges, Ion |  |  | 8 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.8 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 8 | No |  |  |  |  | C_Vacuum
DN-326 | 121.03 | 121.03.06 | Vacuum | BTL | BTL-Beamline Tunnel | BTL/BAL |  | Gauges, Pirani |  |  | 8 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.8 | 0.1 | [7 empty] | 0 | 0 | 100 | 0 | [12 empty] | Flexible <1cm (e.g. RG58) | 8 | No |  |  |  |  | C_Vacuum
DN-327 | 121.03 | 121.03.06 | Vacuum | LG | LG-BTL | BTL/BAL |  | Controller, Ion/Pirani Gauge |  |  | 4 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 78 +/- 5 | 78 +/- 5 |  |  |  | 0 | Air, Environment | 0.1 | 0.4 | 0.1 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 0.5 | 60 | 0.24 | 100 | 0.24 | [12 empty] | Flexible <1cm (e.g. RG58) | 4 | Yes |  |  |  |  | C_Vacuum
JH-001 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Skids | Vane Cooling Skid |  | 1 | Final | Off the Shelf | 5% | Floor | 70 | 24 | 60 | 600 |  | Yes | Sealed concrete | 65 | 78 | 60 max |  |  |  | Air, Environment | 1.12 | 1.12 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 7 | 5819.6907 | 5.8197 | 100 | 5.8197 |  |  |  |  | Yes | [9 empty] | Yes |  |  |  |  | C_WFE
JH-002 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Skids | Vane Cooling Skid |  | 0 | Final | Off the Shelf | 5% | [14 empty] | Chilled LCW | 38 | 38 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 0.6 | 100 | 0.6 | [14 empty] | Yes |  |  |  | Added 120V circuit for controls | C_WFE
JH-003 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Skids | Wall Cooling Skid |  | 1 | Final | Off the Shelf | 5% | Floor | 88 | 24 | 70 | 1200 |  | Yes | Sealed concrete | 65 | 78 | 60 max |  |  |  | Air, Environment | 2.24 | 2.24 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 13.4 | 11140.5508 | 11.1406 | 100 | 11.1406 |  |  |  |  | Yes | [9 empty] | Yes |  |  |  |  | C_WFE
JH-004 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Skids | Wall Cooling Skid |  | 0 | Final | Off the Shelf | 5% | [14 empty] | Chilled LCW | 65 | 65 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 0.6 | 100 | 0.6 | [14 empty] | Yes |  |  |  | Heat load assumes 30% contingency. Added 120V circuit for controls | C_WFE
JH-005 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Skids | Intermediate Cooling Skid |  | 0 | Preliminary | Prototype-Testing | 25% | Floor | 84 | 36 | 78 | 1800 |  | Yes | Sealed concrete | 65 | 78 | 60 max |  |  |  | Air, Environment | 3 | 3 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 0.6 | 100 | 0.6 | [14 empty] | Yes |  |  |  | Added 120V circuit for controls | C_WFE
JH-006 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Skids | Intermediate Cooling Skid |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 175 | 29 | 66 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Chilled LCW | 0 | 0 |  | 86 | 90 | 1 | 10 | 480 V - 3 Phase - 3 Wire | 480 | 60 | 49883.0633 | 49.8831 | 100 | 49.8831 |  |  | 60 |  | Yes | [9 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_WFE
JH-007 | 121.04 | 121.04.03 | BldgI | CP | UP | LCW |  | Pump | Circulating Pump |  | 3 | Preliminary | Prototype-Testing | 25% | Floor | 98 | 26 | 40 |  |  | Yes | Sealed concrete | 65 | 115 | 75 |  |  |  | Air, Environment | 37 | 111 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 224 | 186230.1028 | 558.6903 | 100 | 558.6903 |  |  |  |  | Yes | Yes | [8 empty] | Yes |  |  |  | 3 pumps | C_BldgI
JH-008 | 121.04 | 121.4.03 | BldgI | CP | UP | LCW |  | Pump | Standby Circulating Pump | 3 | 1 | Preliminary | Prototype-Testing | 25% | Floor | 98 | 26 | 40 |  |  | Yes | Sealed concrete | 65 | 115 | 75 | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 |  |  |  |  | Yes | Yes | [8 empty] | No |  |  |  | 1 standby spare. Allocated only space for spare
JH-009 | 121.04 | 121.04.03 | BldgI | CP | UP | LCW |  | Tank | Expansion Tank |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 72 | 72 | 120 | 15000 |  | No | Sealed concrete | 65 | 115 | 75 | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_BldgI
JH-010 | 121.04 | 121.04.03 | BldgI | CP | UP | LCW |  | Heat Exchanger | LCW Heat Exchanger |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 150 | 48 | 120 | 22000 |  | No | Sealed concrete | 65 | 115 | 75 |  |  |  | ICW |  | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | Based on 10 deg F delta T, 88 F supply temp, 11 MW Heat Load. 40% efficiency on Power Amplifiers | C_BldgI
JH-011 | 121.04 | 121.04.03 | BldgI | CP | UP | Dissolved Oxygen |  | Skids |  |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 42 | 24 | 72 | 1200 |  | Yes | Sealed concrete | 65 | 115 | 75 |  |  |  | ICW | 0.1 | 0.1 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 6.2 | 744 | 0.744 | 100 | 0.744 | [14 empty] | Yes |  |  |  | 1/3 hp, 20% heat load, minimal | C_BldgI
JH-012 | 121.04 | 121.04.03 | BldgI | CP | UP | Resistivity Control |  | Bottles |  |  | 3 | Preliminary | Prototype-Testing | 25% | Floor | 18 | 18 | 60 | 300 |  | No | Sealed concrete | 65 | 115 | 75 | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_BldgI
JH-013 | 121.04 | 121.04.03 | BldgI | CP | UP | Compressed Air |  | Air Compressor |  |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 64 | 30 | 60 |  |  | Yes | Sealed concrete | 65 | 115 | 75 |  |  |  | Air, Environment | 12 | 12 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 66.6 | 55370.2002 | 55.3702 | 100 | 55.3702 |  |  |  |  | Yes | Yes | [8 empty] | Yes |  |  |  | out of 40 hp, 80% goes to air (run 1 + 1 standby spare) | C_BldgI
JH-014 | 121.04 | 121.4.03 | BldgI | CP | UP | Compressed Air |  | Air Compressor | Standby | 1 | 1 | Preliminary | Off the Shelf | 5% | Floor | 64 | 30 | 60 |  |  | Yes | Sealed concrete | 65 | 115 | 75 | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 |  |  |  |  | Yes | Yes | [8 empty] | No |  |  |  | 1 standby spare. Allocated only space for spare
JH-015 | 121.04 | 121.04.03 | BldgI | CP | UP | Compressed Air |  | Dryer | Desiccant Dryer |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 27 | 20 | 37 |  |  | Yes | Sealed concrete | 65 | 115 | 75 |  |  |  | Air, Environment | 0.1 | 0.1 | [5 empty] | 240 V - 1 Phase - 2 Wire | 230 | 6.8 | 1564 | 1.564 | 100 | 1.564 | [14 empty] | Yes |  |  |  |  | C_BldgI
JH-016 | 121.04 | 121.4.03 | BldgI | CP | UP | Compressed Air |  | Dryer | Standby Desiccant Dryer | 1 | 1 | Preliminary | Off the Shelf | 5% | Floor | 27 | 20 | 37 |  |  | Yes | Sealed concrete | 65 | 115 | 75 | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | 1 standby spare. Allocated only space for spare
JH-017 | 121.04 | 121.04.03 | BldgI | CP | UP | Compressed Air |  | Tank |  |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 36 | 36 | 80 |  |  | No | Sealed concrete | 65 | 115 | 75 | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_BldgI
JH-018 | 121.04 | 121.04.03 | BldgI | CP | UP | Compressed Air |  | Water/Oil Separator |  |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 32 | 16 | 32 |  |  | No | Sealed concrete | 65 | 115 | 75 | [5 empty] | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 5 | 600 | 0.6 | 100 | 0.6 | [14 empty] | Yes |  |  |  |  | C_BldgI
JH-019 | 121.04 | 121.04.02 | WFE | HBB | HBB-Upper High Bay | Ion Source |  | Skids | Cooling Skid |  | 1 | Final | Off the Shelf | 5% | Floor | 70 | 24 | 60 | 300 |  | Yes | Sealed concrete | 65 | 78 | 60 max |  | 0 | 0 | Air, Environment | 0.4 | 0.4 |  | 72 | 80 | +/- 1 | 10 | 480 V - 3 Phase - 3 Wire | 480 | 3 | 2494.1532 | 2.4942 | 80 | 1.9953 | NA | NA | 20 | N/A | Yes |  | Yes | [7 empty] | Yes | No | Yes | ACNET |  | C_WFE
JH-020 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | Ion Source |  | Cabinets | LV cabinet |  | 2 | Preliminary | Prototype-Testing | 25% | Floor | 31 | 31 | 87 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.1 | 0.2 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 3.6 | 100 | 3.6 |  |  | 15 |  |  | Yes | Yes | [7 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_WFE
JH-021 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | Ion Source |  | Cabinets | HV cabinet |  | 2 | Preliminary | Prototype-Testing | 25% | Floor | 40 | 40 | 87 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.1 | 0.2 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 40 | 33255.3755 | 66.5108 | 100 | 66.5108 |  |  | 40 |  |  | Yes | Yes | [7 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_WFE
JH-022 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | Ion Source |  | Ion Source | Ion source enclosure |  | 2 | Conceptual | Prototype-Testing | 25% | Floor | 28 | 29 | 103 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment |  | 0 | [8 empty] | 0 | 0 | 100 | 0 | [5 empty] | Yes | [8 empty] | No |  |  |  |  | C_WFE
JH-023 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | Ion Source |  | Ion Source | Ion source (all components) |  | 0 | Final | Prototype-Testing | 25% | [8 empty] | 65 | 78 | 60 max |  |  |  | Chilled LCW | 12 | 24 |  | 72 | 80 | +/- 1 |  |  |  |  | 0 | 0 | 100 | 0 | [6 empty] | Yes | [7 empty] | No |  |  |  |  | C_WFE
JH-024 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | Ion Source |  | Bottle Enclosure | Hydrogen bottle enclosure |  | 1 | Conceptual | Prototype-Testing | 25% | Floor | 21 | 17 | 30 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment |  | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-025 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | Ion Source |  | Panels | Electrical panel for Bias PS/CDC |  | 2 | Preliminary | Prototype-Testing | 25% | Suspended | 24 | 24 | 10 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.05 | 0.1 | [5 empty] | 208 V - 1 Phase - 2 Wire | 208 | 15 | 3120 | 6.24 | 100 | 6.24 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_WFE
JH-026 | 121.04 | 121.04.02 | WFE | HBB | HBB-Upper High Bay | LEBT |  | Racks | Rack with solenoid power supplies |  | 1 | Final | Off the Shelf | 5% | Floor | 24 | 32 | 63 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 480 V - 3 Phase - 3 Wire | 480 | 48 | 39906.4506 | 39.9065 | 100 | 39.9065 |  |  | 60 | [11 empty] | Yes | No |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the controllers | C_WFE
JH-027 | 121.04 | 121.04.02 | WFE | HBB | HBB-Upper High Bay | LEBT |  | Racks | Rack with solenoid power supplies controllers |  | 1 | Final | Off the Shelf | 5% | Floor | 24 | 32 | 63 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 15 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the power supplies | C_WFE
JH-028 | 121.04 | 121.04.02 | WFE | HBB | HBB-Upper High Bay | LEBT |  | Racks | Rack with Dipole power supply and controller |  | 1 | Final | Off the Shelf | 5% | Rack Mounted | 24 | 30 | 14 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Spatial requirements for "Height" is the height occupied within the rack; Power requirement is from breaker rating at PIP2IT | C_WFE
JH-029 | 121.04 | 121.04.02 | WFE | HBB | HBB-Upper High Bay | LEBT |  | Racks | Rack with correctors power supplies |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 24 | 30 | 84 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 480 V - 3 Phase - 3 Wire | 480 | 48 | 39906.4506 | 39.9065 | 100 | 39.9065 |  |  | 60 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the controllers | C_WFE
JH-030 | 121.04 | 121.04.02 | WFE | HBB | HBB-Upper High Bay | LEBT |  | Racks | Rack with correctors power supplies controllers |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 24 | 30 | 84 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the power supplies | C_WFE
JH-031 | 121.04 | 121.04.02 | WFE | HBB | HBB-Upper High Bay | WFE |  | Racks | Rack with stepper motor bulk power supply |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 24 | 30 | 75 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the controllers | C_WFE
JH-032 | 121.04 | 121.04.02 | WFE | HBB | HBB-Upper High Bay | WFE |  | Racks | Rack with stepper motor controllers |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 24 | 30 | 75 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the power supplies | C_WFE
JH-033 | 121.04 | 121.04.02 | WFE | HBB | HBB-Upper High Bay | LEBT |  | Power Supplies | LEBT chopper power supply |  | 1 | Preliminary | Off the Shelf | 5% | Rack Mounted | 19 | 30 | 3.5 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.05 | 0.05 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Within WFE footprint | C_WFE
JH-034 | 121.04 | 121.04.02 | WFE | HBB | HBB-Upper High Bay | LEBT |  | Power Supplies | LEBT chopper DC offset power supply |  | 1 | Preliminary | Off the Shelf | 5% | Rack Mounted | 19 | 30 | 3.5 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.05 | 0.05 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Within WFE footprint | C_WFE
JH-035 | 121.04 | 121.04.02 | WFE | HBB | HBB-Upper High Bay | WFE |  | Cabinets | Rittal cabinet for LCW (including RFQ skid controller) |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 103 | 16 | 83 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_WFE
JH-036 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Couplers | Power coupler body |  | 2 | Final | Off the Shelf | 5% | RFQ Mounted | [7 empty] | 65 | 78 | 60 max |  |  |  | LCW | 0.3 | 0.6 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-037 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Couplers | Power coupler antenna |  | 2 | Final | Off the Shelf | 5% | RFQ Mounted | [7 empty] | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.12 | 0.24 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-038 | 121.04 | 121.04.02 | WFE | HBB | HBB-Upper High Bay | RFQ |  | Power Supplies | RFQ couplers bias power supply |  | 1 | Final | Off the Shelf | 5% | Rack Mounted | 24 | 30 | 5 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.05 | 0.05 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Single unit in standard rack; Power requirement is from breaker rating at PIP2IT | C_WFE
JH-039 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Power Amplifiers |  |  | 2 | Final | Off the Shelf | 5% | Floor | 94 | 40 | 90 |  |  |  |  | 65 | 78 | 60 max |  |  |  | LCW | 150 | 300 |  | 86 |  | 1 | 10 | 480 V - 3 Phase - 3 Wire | 480 | 180 | 149649.1898 | 299.2984 | 100 | 299.2984 |  |  |  |  | Yes | [9 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_WFE
JH-040 | 121.03 | 121.03.05 | Magnets | HBB | HBB-Upper High Bay | MEBT |  | Racks | Rack with quadrupole power supplies and controllers |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 24 | 30 | 75 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_Magnets
JH-041 | 121.03 | 121.03.05 | Magnets | HBB | HBB-Upper High Bay | MEBT |  | Racks | Rack with dipole correctors power supplies and controllers |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 24 | 30 | 75 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT | C_Magnets
JH-042 | 121.03 | 121.03.05 | Magnets | HBB | HBB-Upper High Bay | MEBT |  | Racks | Rack with dipole correctors bulk power supply |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 24 | 30 | 75 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the correctors power supplies and controllers | C_Magnets
JH-043 | 121.03 | 121.03.05 | Magnets | HBB | HBB-Upper High Bay | MEBT |  | Racks | Rack with dipole correctors bulk power supply |  | 1 | Preliminary | Prototype-Testing | 25% | Floor | 24 | 30 | 75 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | Power requirement is from breaker rating at PIP2IT; In the same rack as the correctors power supplies and controllers | C_Magnets
JH-044 | 121.04 | 121.04.02 | WFE | HBB | HBB-Upper High Bay | MEBT |  | Racks | Rack with bunching cavities amplifiers and controllers |  | 2 | Preliminary | Off the Shelf | 5% | Floor | 24 | 30 | 99 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 1 | 0.5 |  |  |  |  | 208 V - 3 Phase - 3 Wire | 208 | 30 | 10807.997 | 21.616 | 100 | 21.616 |  |  | 30 | [11 empty] | Yes |  |  |  | Standard rack; Power requirement is from breaker rating at PIP2IT | C_WFE
JH-045 | 121.04 | 121.04.02 | WFE | HBB | HBB-Upper High Bay | WFE |  | Racks | Rack with electrodes biasing power supplies and current readouts electronics |  | 1 | Preliminary | Off the Shelf | 5% | Floor | 24 | 30 | 99 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.5 | 0.5 | 0.5 |  |  |  |  | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 1.8 | 100 | 1.8 |  |  | 20 | [11 empty] | Yes |  |  |  | All units occupy 1/2 rack | C_WFE
JH-046 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | MEBT |  | Bunching Cavities |  |  | 4 | Final | Prototype-Testing | 25% | Beamline/Tunnel | [7 empty] | 65 | 78 | 60 max |  |  |  | LCW | 1.5 | 6 |  | 86 | 88 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-047 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | MEBT |  | Scrapers Vacuum Chamber |  |  | 4 | Final | Prototype-Testing | 25% | Beamline/Tunnel | [7 empty] | 65 | 78 | 60 max |  |  |  | LCW | 0.3 | 1.2 |  | 86 | 88 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-048 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | MEBT |  | Absorber Assembly |  |  | 1 | Preliminary | Prototype-Testing | 25% | Beamline/Tunnel | [7 empty] | 65 | 78 | 60 max |  |  |  | LCW | 20 | 20 |  | 86 | 88 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | 10 gpm | C_WFE
JH-049 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | MEBT |  | Kickers |  |  | 2 | Final | Prototype-Testing | 25% | Beamline/Tunnel | [7 empty] | 65 | 78 | 60 max |  |  |  | LCW | 0.5 | 1 |  | 86 | 88 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-050 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | LEBT |  | Solenoids |  |  | 4 | Final | Off the Shelf | 5% | Rack Mounted | [7 empty] | 65 | 78 | 60 max |  |  |  | LCW | 7.5 | 30 |  | 86 | 88 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-051 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | LEBT |  | Magnets | Bending dipole |  | 1 | Final | Prototype-Testing | 25% | Beamline/Tunnel | [7 empty] | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.05 | 0.05 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-052 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | LEBT |  | Chopper |  |  | 1 | Final | Off the Shelf | 5% | Beamline/Tunnel | [7 empty] | 65 | 78 | 60 max |  |  |  | LCW | 0.3 | 0.3 |  | 86 | 88 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-053 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | Ion Source |  | Allison Scanner |  |  | 4 | Final | Prototype-Testing | 25% | Beamline/Tunnel | 24 | 30 | 98 |  |  |  |  | 65 | 78 | 60 max |  |  |  | LCW | 0.6 | 2.4 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-054 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | RFQ |  | Circulators |  |  | 2 | Preliminary | Prototype-Testing | 25% | Suspended | 11 | 30 | 34 |  |  |  |  | 65 | 78 | 60 max |  |  |  | LCW | 0 | 0 |  | 86 |  | 1 | 10 |  |  |  | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_WFE
JH-055 | 121.04 | 121.04.02 | WFE | HBB | HBB-Lower High Bay | MEBT |  | Power Supplies | Chopper HV Power supplies |  | 4 | Preliminary | Prototype-Testing | 25% | Suspended | 24 | 30 | 5 |  |  |  |  | 65 | 78 | 60 max |  |  |  | Air, Environment | 0.1 | 0.4 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 15 | 1800 | 7.2 | 100 | 7.2 |  |  | 20 | [11 empty] | Yes |  |  |  |  | C_WFE
JH-056 | 121.04 | 121.04.03 | BldgI | LG | LG-General |  | AC Distribution |  | HLA for AC Distribution Cables |  |  | Preliminary | Expert Opinion | 50% | [14 empty] | Air, Environment |  | 0 | 120 | [7 empty] | 0 | 0 |  | 0 | [14 empty] | No |  |  |  |  | C_BldgI
JO-001 | 121.02 | 121.02.02 | HWR | LT | LT-HWR | HWR Cryomodule |  | Cryomodule |  |  | 1 | Final | Off the Shelf | 5% | Floor | 244.1 | 78.74 | 78.74 | 18580 |  | TBD | Sealed concrete | [7 empty] | NA | 0 |  | 70 | 75 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No | Yes | No | NA | CM Space requirement is CM only - no "keep clear" or access volume added. Air cooling is for coupler, 800SCFH total. | C_HWR
JO-002 | 121.02 | 121.02.02 | HWR | LT | LT-HWR | HWR Cryomodule |  | Couplers | 8 cavities x 1 CM |  | 8 | Final | Prototype-Testing | 25% | [14 empty] | Air, Environment | 0.025 | 0.2 | 0.2 | 70 | 75 | [5 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | Air cooling is for coupler, 800SCFH (13.3 SCFM) total, < 40deg F dew point, compressed air | C_HWR
JO-003 | 121.02 | 121.02.04 | Elliptical | LT | LT-LB650 | LB650 Cryomodule |  | Cryomodule |  |  | 9 | Conceptual | Expert Opinion | 50% | Floor | 255 | 82 | 88 | 21000 |  | TBD | Sealed concrete | [8 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No | Yes | No | NA |  | C_Elliptical
JO-004 | 121.02 | 121.02.04 | Elliptical | LT | LT-HB650 | HB650 Cryomodule |  | Cryomodule |  |  | 6 | Preliminary | Off the Shelf | 5% | Floor | 391 | 82 | 88 | 27700 |  | TBD | Sealed concrete | [8 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 |  |  |  |  | No | No | No | [7 empty] | No | Yes | No | NA |  | C_Elliptical
JO-005 | 121.02 | 121.02.04 | Elliptical | LT | LT-LB650 | LB650 Cryomodule |  | Couplers | 4 cavities x 9 CMs |  | 36 | Conceptual | Expert Opinion | 50% | [14 empty] | Air, Compressed | 0.30667 | 11.04 |  | 70 | 75 | [5 empty] | 0 | 0 | 100 | 0 |  |  |  |  | No | No | No | [7 empty] | No | No | No | NA | Air flow = 16.5 SCFM per cryomodule (for 9 CMs use 149 cfm) | C_Elliptical
JO-006 | 121.02 | 121.02.04 | Elliptical | LT | LT-HB650 | HB650 Cryomodule |  | Couplers | 6 cavities x 4 CMs |  | 24 | Preliminary | Prototype-Testing | 25% | [14 empty] | Air, Compressed | 0.45833 | 11 |  | 70 | 75 | [5 empty] | 0 | 0 | 100 | 0 |  |  |  |  | No | No | No | [7 empty] | No | No | No | NA | Air flow = 33 SCFM per cryomodule (for 6 CMs use 198 cfm) | C_Elliptical
JO-007 | 121.02 | 121.02.03 | SSR | LT | LT-SSR1 | SSR1 Cryomodule |  | Cryomodule |  |  | 2 | Final | Off the Shelf | 5% | Floor | 212.6 | 86.6 | 112.2 | 26400 |  | TBD | Sealed concrete | [8 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No | Yes | No | NA |  | C_SSR
JO-008 | 121.02 | 121.02.03 | SSR | LT | LT-SSR2 | SSR2 Cryomodule |  | Cryomodule |  |  | 7 | Preliminary | Off the Shelf | 5% | Floor | 255.9 | 86.6 | 112.2 | 26400 |  | TBD | Sealed concrete | [8 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 |  |  |  |  | No | No | No | [7 empty] | No | Yes | No | NA |  | C_SSR
JO-009 | 121.02 | 121.02.03 | SSR | LT | LT-SSR1 | SSR1 Cryomodule |  | Couplers | 8 cavities x 2 CMs |  | 16 | Final | Prototype-Testing | 25% | [14 empty] | Air, Compressed | 0.051 | 0.816 |  | 70 | 75 | [5 empty] | 0 | 0 | 100 | 0 |  |  |  |  | No | No | No | [7 empty] | No | No | No | NA | Air flow = 16 SCFM per cryomodule (for 2 CMs use 16 cfm) | C_SSR
JO-010 | 121.02 | 121.02.03 | SSR | LT | LT-SSR2 | SSR2 Cryomodule |  | Couplers | 5 cavities x 7 CMs |  | 35 | Preliminary | Prototype-Testing | 25% | [14 empty] | Air, Compressed | 0.18 | 6.3 |  | 70 | 75 | [5 empty] | 0 | 0 | 100 | 0 |  |  |  |  | No | No | No | [7 empty] | No | No | No | NA | Air flow = 15 SCFM per cryomodule (for 7 CMs use 105 cfm) | C_SSR
JO-011 | 121.02 | 121.2.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Cold Box Equipment |  |  | 1 | Final | Off the Shelf | 5% | Floor | 590.4 | 315 | 276 | 165347 | F(F) 25, F(L) 20 |  | Sealed concrete | [6 empty] | Chilled Water |  | 0 |  | 60 |  |  |  | 480 V - 3 Phase - 3 Wire | 480 | 70 | 58196.9071 | 58.1969 | 100 | 58.1969 |  |  |  |  | Yes | [9 empty] | Yes | No |  |  | 60 gpm for entire cold box station at 60 deg F or higher | C_CP
JO-012 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Cold Box Equipment |  |  | 1 | Final | Off the Shelf | 5% | [8 empty] | 78 | 68 | 55 | [5 empty] | 0 | [5 empty] | 240 V - 1 Phase - 2 Wire | 240 | 10 | 2400 | 2.4 | 100 | 2.4 |  |  |  |  | Yes | [9 empty] | Yes | No |  |  |  | C_CP
JO-013 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Cold Box Equipment |  |  | 1 | Final | Off the Shelf | 5% | [8 empty] | 78 | 68 | 55 | [5 empty] | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 110 | 13200 | 13.2 | 100 | 13.2 |  |  |  |  | Yes | [9 empty] | Yes | No |  |  |  | C_CP
JO-014 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Cold Box Equipment |  |  | 1 | Final | Off the Shelf | 5% | [8 empty] | 78 | 68 | 55 |  | 45,000 cfm in upper 10,000 cfm in lower portion |  | Air, Environment | 15 | 15 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No | No |  |  |  | C_CP
JO-015 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Cold Box Station |  | 4.5K Cold Box |  |  | 1 | Final | Off the Shelf | 5% | Floor | 74.4 | 63.6 | 188.4 | 6266 |  |  |  | 78 | 68 | 55 | [5 empty] | 0 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 3.6 | 2992.9838 | 2.993 | 100 | 2.993 |  |  |  |  | Yes | [9 empty] | Yes | No |  |  |  | C_CP
JO-016 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Cold Box Station |  | 4.5K Cold Box |  |  | 1 | Final | Off the Shelf | 5% | [8 empty] | 78 | 68 | 55 | [5 empty] | 0 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 30 | 3600 | 3.6 | 100 | 3.6 |  |  |  |  | Yes | [9 empty] | Yes | No |  |  |  | C_CP
JO-017 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Racks, Rittal | Cryo Control Cab |  | 1 | Final | Off the Shelf | 5% | Floor | 32.2 | 21 | 88.8 | 50 |  |  |  | 78 | 68 | 55 |  |  |  | Air, Environment | 0.5 | 0.5 | [5 empty] | 120 V - 1 Phase - 2 Wire | 120 | 30 | 3600 | 3.6 | 100 | 3.6 |  |  |  |  | Yes | [9 empty] | Yes | No |  |  |  | C_CP
JO-018 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Storage Tank | Lhe |  | 1 | Conceptual | Completely Unknown | 100% | Floor | [7 empty] | 78 | 68 | 55 | [5 empty] | 0 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 6 | 4988.3063 | 4.9883 | 100 | 4.9883 | [14 empty] | Yes | No |  |  |  | C_CP
JO-019 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Welding Receptacle |  |  | 1 | Final | Off the Shelf | 5% | Suspended | [7 empty] | 78 | 68 | 55 | [5 empty] | 0 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 60 | 49883.0633 | 49.8831 | 100 | 49.8831 |  |  |  |  | Yes | [9 empty] | Yes | No |  |  |  | C_CP
JO-020 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Cold Box Station |  | Generator | For UPS |  | 1 | Conceptual | Completely Unknown | 100% | Floor | [7 empty] | 78 | 68 | 55 | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | 25 |  |  |  | Yes | TBD | [8 empty] | No | No |  |  |  | C_CP
JO-021 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Compressors | Mycom |  | 1 | Final | Off the Shelf | 5% | Floor | 139.2 | 69.6 | 88.8 | 7000 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None |  |  |  | ICW | 83 | 83 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 600 | 498830.6326 | 498.8306 | 100 | 498.8306 | [14 empty] | Yes |  |  |  | ICW @ 200 gpm | C_CP
JO-022 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | SP |  | 1 | Final | Off the Shelf | 5% | Floor | 220.8 | 122.4 | 174 | 26455 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None |  |  |  | ICW | 917 | 917 | [5 empty] | Other (specify) | 4160 | 55.5 | 399895.8905 | 399.8959 | 100 | 399.8959 | [14 empty] | Yes |  |  |  | ICW @ 240 gpm | C_CP
JO-023 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | LP |  | 1 | Final | Off the Shelf | 5% | Floor | 220.8 | 122.4 | 174 | 26455 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | ICW @ 240 gpm | C_CP
JO-024 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | HP |  | 2 | Final | Off the Shelf | 5% | Floor | 220.8 | 122.4 | 174 | 26455 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None |  |  |  | ICW | 1400 | 2800 | [5 empty] | Other (specify) | 4160 | 100 | 720533.1359 | 1441.0663 | 100 | 1441.0663 | [14 empty] | Yes |  |  |  | ICW @ 480 gpm | C_CP
JO-025 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Panels | Gas Mgmt |  | 2 | Final | Off the Shelf | 5% | Floor | 196.8 | 39.6 | 86.4 | 3750 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_CP
JO-026 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | Oil Absorber |  | 1 | Final | Off the Shelf | 5% | Floor | 91.2 | 76.8 | 146.4 | 8160 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 37 | 30761.2223 | 30.7612 | 100 | 30.7612 | [14 empty] | Yes |  |  |  |  | C_CP
JO-027 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | Oil Coalscr |  | 1 | Final | Off the Shelf | 5% | Floor | 139.2 | 40.8 | 110.4 | 5511 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_CP
JO-028 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | Oil Dryer |  | 1 | Final | Off the Shelf | 5% | Floor | 74.4 | 78 | 100.8 | 1984 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_CP
JO-029 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | LP Oil Absrbr |  | 3 | Final | Off the Shelf | 5% | Floor | 393.6 | 141.6 | 178.8 | 39685 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 37 | 30761.2223 | 92.2837 | 100 | 92.2837 | [14 empty] | Yes |  |  |  |  | C_CP
JO-030 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Racks, Rittal | SP/LP Control Cab |  | 1 | Final | Off the Shelf | 5% | Floor | 189.6 | 24 | 86.4 | 2200 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None |  |  |  | Air, Environment | 0.5 | 0.5 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 20 | 16627.6878 | 16.6277 | 100 | 16.6277 | [14 empty] | Yes |  |  |  |  | C_CP
JO-031 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Racks, Rittal | HP Control Cab |  | 1 | Final | Off the Shelf | 5% | Floor | 157.2 | 24 | 86.4 | 2200 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None |  |  |  | Air, Environment | 0.5 | 0.5 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 20 | 16627.6878 | 16.6277 | 100 | 16.6277 | [14 empty] | Yes |  |  |  |  | C_CP
JO-032 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Racks, Rittal | Inventory Ctrl Cab |  | 1 | Final | Off the Shelf | 5% | Floor | 139.2 | 40.8 | 110.4 | 1000 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None |  |  |  | Air, Environment | 0.5 | 0.5 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 20 | 16627.6878 | 16.6277 | 100 | 16.6277 | [14 empty] | Yes |  |  |  |  | C_CP
JO-033 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Skids | Purifier Skid |  | 1 | Final | Off the Shelf | 5% | Floor | 36 | 36 | 117.6 | 2200 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  |  | C_CP
JO-034 | 121.02 | 121.02.05 | CP | CP | UP | Warm Compressor Section |  | Compressors | Air |  | 1 | Final | Off the Shelf | 5% | Floor | 81.6 | 40.8 | 67.2 | 500 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None |  |  |  | Air, Environment | 44 | 44 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 110 | 91452.2826 | 91.4523 | 100 | 91.4523 | [14 empty] | Yes |  |  |  |  | C_CP
JO-035 | 121.02 | 121.02.05 | CP | CP | UP | Warm Compressor Section |  | Compressors | Standby Air Compressor |  | 1 | Final | Off the Shelf | 5% | Floor | 81.6 | 40.8 | 67.2 | 500 | F(F) 25, F(L) 20 |  | Sealed concrete | 68 | Amb + 10 | None | [5 empty] | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No |  |  |  | Allocated space only for 1 standby | C_CP
JO-036 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Welding Receptacle | Weld Receptacle |  | 1 | Final | Off the Shelf | 5% | Suspended | [7 empty] | 68 | Amb + 10 | None | [5 empty] | 0 | [5 empty] | 480 V - 3 Phase - 3 Wire | 480 | 60 | 49883.0633 | 49.8831 | 100 | 49.8831 | [14 empty] | Yes |  |  |  |  | C_CP
JO-037 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Warm Compressor Section |  | Entire Area |  |  | 1 | Final | Off the Shelf | 5% | [8 empty] | 68 | Amb + 10 | None |  | 45,000 cfm in upper 10,000 cfm in lower portion |  | Air, Environment | 200 | 200 | [8 empty] | 0 | 0 | 100 | 0 | 25 | [13 empty] | No | No |  |  |  | C_CP
JO-038 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Network Room |  | Entire Area |  |  | 1 | Final | Off the Shelf | 5% | [8 empty] | 68 | 78 | 55 | Yes |  |  |  |  | 0 | [8 empty] | 0 | 0 | 100 | 0 | [14 empty] | No | No |  |  |  | C_CP
JO-039 | 121.02 | 121.2.05 | CP | CP | Cryoplant Building | Network Room |  | Racks | Main Network Room | 2 | 1 | Final | Off the Shelf | 5% | Floor | 24 | 48 | 96 | [10 empty] | Air, Environment | 0.5 | 0.5 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 30 | 3.2 | 166.2769 | 0.16628 | 100 | 0.16628 | [7 empty] | Other | Open | Left AND Right | Closed | Yes |  |  | No |  |  |  | 1-30A/208V ckt fed from UPS, 1 30A/208V ckt fed from bldg pwr, 1 20A/120V ckt fed from bldg pwr | C_CP
JO-040 | 121.02 | 121.02.05 | CP | CP | Cryoplant Building | Network Room |  | Racks | Cryo Specific Rack |  | 1 | Final | Off the Shelf | 5% | Floor | 24 | 48 | 96 | [10 empty] | Air, Environment | 0.5 | 0.5 | [5 empty] | 208Y/120 V - 3 Phase - 4 Wire | 30 | 3.2 | 166.2769 | 0.16628 | 100 | 0.16628 | [7 empty] | Other | Open | Left AND Right | Closed | Yes |  |  | No |  |  |  | 1-30A/208V ckt fed from UPS, 1 30A/208V ckt fed from bldg pwr, 1 20A/120V ckt fed from bldg pwr | C_CP
LG
LT
SSR2
LB650
HB650
HWR
High Bay Building
HBB-lower - WFE
SSR1
Note on AZ16: Racks should be listed as a separate row to ensure the location and quantity are captured correctly.
Note on AJ17: This is a stability requirement of the water supply temperature, and may not be necessary in most cases. Format shall be +/- in degrees F.
Note on BE17: Choose the least flexible cable type
Note on BF21: Duane L. Newhart x6378,3721,6378 11580N: rack only have power and ethernet counted here. One of each per rack
Note on BF24: Duane L. Newhart x6378,3721,6378 11580N: cable type: Thermal couple; 6C16 LVDT/LimitSwitches: 18g multi
Note on BF28: Duane L. Newhart x6378,3721,6378 11580N: plus 1 per supply ethernet and 1 RG58
Note on L29: Fernanda G. Garcia x3798 13038N: Will likely go from 2 to 1. In BCR process now
Note on BF29: Duane L. Newhart x6378,3721,6378 11580N: plus 1 ethernet per supply and 1 RG58
Note on BF30: Duane L. Newhart x6378,3721,6378 11580N: Also 9 twinax cables
Note on BF31: Duane L. Newhart x6378,3721,6378 11580N: 4 twinax
Note on BF32: Duane L. Newhart x6378,3721,6378 11580N: 16 twinax and 4 ethernet 4 gr58 for mps
Note on J35: Fernanda G. Garcia x3798 13038N: highly likely this will not be necessary. Currently in BCR process
Note on BF49: Duane L. Newhart x6378,3721,6378 11580N: rack only have power and ethernet counted here. One of each per rack
Note on BF57: Duane L. Newhart x6378,3721,6378 11580N: Total Cable estimat for all 25 racks…types unknow
Note on BF58: Duane L. Newhart x6378,3721,6378 11580N: Total Cable estimat for all 25 racks…types unknow
Note on BF59: Duane L. Newhart x6378,3721,6378 11580N: Total Cable estimat for all 25 racks…types unknow
Note on BF60: Duane L. Newhart x6378,3721,6378 11580N: Total Cable estimat for all 25 racks…types unknow
Note on BF61: Duane L. Newhart x6378,3721,6378 11580N: Total Cable estimat for all 25 racks…types unknow
Note on L62: Fernanda G. Garcia x3798 13038N: RC - Rack Layout - has the breakdown from M. Kucera
Note on AU63: Duane L. Newhart x6378,3721,6378 11580N: See Notes in last column
Note on Q65: Jonathan W. Hunt x 15287N: Tom Zuchnik stated that the LCW PLC racks will be 32" interior length. Use 40" exterior length
Note on S68: Jonathan W. Hunt x 15287N: Verify with Kucera that 45U is sufficient
Note on AE78: Fernanda G. Garcia x3798 13038N: Fernanda G. Garcia x3798 13038N: According to JS conversation with E. Huedem, the circulator heat load is in series with the load, which dominates the heat load.
Note on L80: Fernanda G. Garcia x3798 13038N: RDR Jan' 19 6
Note on AE83: Fernanda G. Garcia x3798 13038N: According to JS conversation with E. Huedem, the circulator heat load is in series with the load, which dominates the heat load.
Note on T84: Duane L. Newhart x6378,3721,6378 11580N: Estimate based on CMTF
Note on L85: Fernanda G. Garcia x3798 13038N: RDR Jan' 19 12
Note on AE88: Fernanda G. Garcia x3798 13038N: Fernanda G. Garcia x3798 13038N: According to JS conversation with E. Huedem, the circulator heat load is in series with the load, which dominates the heat load.
Note on L90: Fernanda G. Garcia x3798 13038N: RDR Jan' 19 9
Note on AE93: Fernanda G. Garcia x3798 13038N: Fernanda G. Garcia x3798 13038N: According to JS conversation with E. Huedem, the circulator heat load is in series with the load, which dominates the heat load.
Note on T94: Duane L. Newhart x6378,3721,6378 11580N:
Note on L95: Fernanda G. Garcia x3798 13038N: RDR Jan' 19 12
Note on AQ96: Fernanda G. Garcia x3798 13038N: JS: Reference: see email….
Note on T98: Duane L. Newhart x6378,3721,6378 11580N: Estimate based on CMTF
Note on AE98: Fernanda G. Garcia x3798 13038N: Fernanda G. Garcia x3798 13038N: According to JS conversation with E. Huedem, the circulator heat load is in series with the load, which dominates the heat load.
Note on L193: Fernanda G. Garcia x3798 13038N: RC rack built 3
Note on AN193: Fernanda G. Garcia x3798 13038N: 2x 20Amps breaker
Note on L198: Fernanda G. Garcia x3798 13038N: RC rack built shows 6
Note on AN198: Fernanda G. Garcia x3798 13038N: 2x 20Amps breaker
Note on AN203: Fernanda G. Garcia x3798 13038N: 2x 20Amps breaker
Note on J352: Fernanda G. Garcia x3798 13038N: Are these part of the 3 right angle valves/CM?

## HPRF-July 12-2019
| Amplifier Efficiency |  | Power Loss Factor to Air |  |  |  | J. Steimel | Jul-12-2019
| 0.44 |  | 0.07
| HB650 Combining Efficiency | [7 empty] | CW (2mA beam) |  |  |  | Pulsed beam
| 0.875 |  |  |  | SSA | Number of | Number of | TOTAL | Heat Load to WATER | Heat Load to AIR | Heat Load to WATER | Heat Load to AIR | Heat Load to WATER | Heat Load to AIR | Heat Load to WATER | Heat Load to AIR | Expected | Heat Load to Water | TOTAL |  | Electrical
[5 empty] | Rated Power | SSA | 20kW | Wall Power (CW beam) | per SSA Unit | per SSA Unit | TOTAL SSA | TOTAL SSA | per SSA Unit | per SSA Unit | TOTAL SSA | TOTAL SSA | Reflected* | TOTAL SSA | Water flow |  | Amperage
[7 empty] | Modules | Pwall-max | Pwater-air | Pwater-air | Pwater-air | Pwater-air | Pwater-air | Pwater-air | Pwater-air | Pwater-air | Pamp-pulsed | from Refl. Pwr |  |  | per SSA
[5 empty] | (kW) |  | per SSA Unit | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (kW) | (gpm) |  | (Amps)
[5 empty] | 7 | 24 | 0.33 | 381.8182 | 8.2855 | 0.62364 | 198.8509 | 14.9673 | 8.2855 | 0.62364 | 198.8509 | 14.9673 | 1 | 24 | 166.88 | ** | 21.2618
[5 empty] | 20 | 35 | 1 | 1590.9091 | 23.6727 | 1.7818 | 828.5455 | 62.3636 | 23.6727 | 1.7818 | 828.5455 | 62.3636 | 4 | 140 | 805 |  | 60.7481
[5 empty] | 40 | 36 | 2 | 3272.7273 | 47.3455 | 3.5636 | 1704.4364 | 128.2909 | 47.3455 | 3.5636 | 1704.4364 | 128.2909 | 11 | 396 | 1656 |  | 127.1473
[5 empty] | 70 | 36 | 4 | 6545.4545 | 103.9909 | 6.2364 | 3743.6727 | 224.5091 | 103.9909 | 6.2364 | 3743.6727 | 224.5091 | 18 | 648 | 3312 |  | 254.2945
|  |  |  | TOTAL | 137 | 131 |  | 11790.9091 | 183.2945 | 12.2055 | 6475.5055 | 430.1309 | 183.2945 | 12.2055 | 6475.5055 | 430.1309 | 34 | 1208 | 5939.88 |  | 463.4518
|  |  |  | GRAND TOTAL Power to Water - Pulsed Mode | 7683.5055 | kW
|  |  |  | GRAND TOTAL Power to Air - Pulsed Mode | 430.1309 | kW
|  |  |  | GRAND TOTAL Power to Water - CW Mode | 6475.5055 | kW
|  |  |  | GRAND TOTAL Power to Air - CW Mode | 430.1309 | kW
REFERENCES
Formula extract from EP presentation
| ηHVDC | 0.95
JS email: 08/27/2019: The heat lost to water through the amplifier is Pstation*((1-eta)/eta) for both pulsed and CW. In CW mode, the extra wall power goes into the beam. In pulsed mode, you have the extra cooling required to handle the reflected power into the load.
* | Estimate reflected power comes from an analysis conducted by E. Pozdeyeve - | [5 empty] | File: SP: | Accelerator Physics - Cooling Requirements (07/01/2019)
Source: JS - ISD
** HWR (TOMCO) mimimum required flow is 15l/min (3.96 gpm) | [5 empty] | ED0010250 (ISD)
** SSR1 minimum flow is 32 l/min (8.45 gpm) | [5 empty] | ED0006356 (ICD)
wall= Pamp+[Pstation*( (η-1)/η) ]*ηHVDC
𝑃wall= Pamp+[Pstation*( (η-1)/η) ]*ηHVDC
wall-max= Pstation/η
𝑃wall-max= Pstation/η
water-air= wall-max - Pstation= Pstation*( (1-η)/η)
𝑃water-air= 𝑃wall-max - Pstation= Pstation*( (1-η)/η)
wall-pulsed= Pamp-pulsed+Pwater-air
𝑃wall-pulsed= Pamp-pulsed+Pwater-air
Note on I12: Fernanda G. Garcia x3798 13038N: Fernanda G. Garcia x3798 13038N: [7/12] According to AK, 70kW amplifiers will have a more powerful unit. A total of 3 RF SSA compose the 70kW at an efficiency of 44%. Leaving 4 units as-is for this calculation purpose.

## HPRF-July12-2019 (hidden)
Amplifier Efficiency |  | Power Loss Factor to Air |  |  | J. Steimel | Jul-12-2019
0.44 |  | 0.07
HB650 Combining Efficiency |  |  | SSA Rated Power (kW) | Number of SSA | Number of 20kW Modules | SSA Total Power (kW) | SSA Power to air (CW 2mA beam) (kW) | Heat Load to Air per SSA (CW 2mA beam) (kW) | SSA Power to air (Pulsed beam) (kW) | SSA Power to water (Pulsed beam) (kW) | Expected Reflected Power | Load Power to Water (W) | Water flow (gpm) | Electrical Amps/SSA
0.875 |  |  | 7 | 24 |  | 381.8182 | 26.7273 | 1.1136 | 14.9673 | 198.8509 | 1 | 24 |  | 21.2618
|  |  | 20 | 35 | 1 | 1590.9091 | 111.3636 | 3.1818 | 62.3636 | 828.5455 | 4 | 140 | 805 | 60.7481
|  |  | 40 | 36 | 2 | 3272.7273 | 229.0909 | 6.3636 | 128.2909 | 1704.4364 | 11 | 396 | 1656 | 127.1473
|  |  | 70 | 36 | 4 | 5727.2727 | 400.9091 | 11.1364 | 224.5091 | 2609.9182 | 18 | 648 | 3312 | 222.5077
[6 empty] | 10972.7273 | 768.0909 | 21.7955 | 430.1309 | 5341.7509 |  | 1208 | 5773 | 431.6649
ηHVDC | 0.95 | [9 empty] | TOTAL Power to Water (W) | 6549.7509
wall= Pamp+[Pstation*( (η-1)/η) ]*ηHVDC
𝑃wall= Pamp+[Pstation*( (η-1)/η) ]*ηHVDC
Note on B3: Duane L. Newhart x6378,3721,6378 11580N: Modified efficiency from 43 to 40.82 % to accound for the HV-DC conversion efficiency
Note on H9: Fernanda G. Garcia x3798 13038N: [7/12] According to AK, 70kW amplifierw will have a more powerful unit and 3 RF amplifiers at efficiency of 44%. Leaving 4 units as-is for this calculation purpose.

## HPRF-Apr12-2019
Amplifier Efficiency |  | Power Loss Factor to Air |  |  | J. Steimel | Apr-12-2019
0.40825 |  | 0.1
HB650 Combining Efficiency |  |  | Amplifier Rated Power (kW) | Number of Amps | Number of 20kW Modules | Total Power (W) | Power to Air (CW Beam 2mA) (W) | Power to Air (Pulsed Beam) (W) | Amplifier Power to Water (W) | Expected Reflected Power | Load Power to Water (W) | Water flow (gpm)
0.875 |  |  | 7 | 24 |  | 411.5126 | 41.1513 | 24.3513 | 202.3613 | 1 | 24
|  |  | 20 | 35 | 1 | 1714.6356 | 171.4636 | 101.4636 | 843.1721 | 4 | 140 | 805
|  |  | 40 | 33 | 2 | 3233.3129 | 323.3313 | 191.3313 | 1589.9816 | 11 | 363 | 1518
|  |  | 80 | 36 | 4 | 7054.5009 | 705.4501 | 417.4501 | 3829.0508 | 18 | 648 | 3312
[6 empty] | 12413.962 | 1241.3962 | 734.5962 | 6464.5658 |  | 1175 | 5635 | Total Power to Water (W) | 7639.5658
ηHVDC | 0.95
wall= Pamp+[Pstation*( (η-1)/η) ]*ηHVDC
𝑃wall= Pamp+[Pstation*( (η-1)/η) ]*ηHVDC
Note on B3: Duane L. Newhart x6378,3721,6378 11580N: Modified efficiency from 43 to 40.82 % to accound for the HV-DC conversion efficiency

## Dropdown Lists
Dropdown List Tables
WBS Names and IDs |  |  | General |  | Space Designations |  | Level of Design | Uncertainty Multipliers |  |  | Source of Requirements | Uncertainty Multipliers
HWR | 121.02.02 |  | Yes |  | HBB-Lower High Bay |  | Pre-conceptual | 100% |  |  | Off the Shelf | 5%
SSR | 121.02.03 |  | No |  | HBB-Upper High Bay |  | Conceptual | 50% |  |  | Prototype-Testing | 25%
Elliptical | 121.02.04 |  | TBD |  | HBB-Control Room |  | Preliminary | 30% |  |  | Expert Opinion | 50%
CP | 121.02.05 |  | N/A |  | HBB-Tech Support Space |  | Final | 15% |  |  | Completely Unknown | 100%
CDS | 121.02.06 |  |  |  | HBB-Computer Space
HPRF | 121.03.03 |  | None |  | HBB-Exterior Space
LLRF | 121.03.04 |  | N/A |  | LT-HWR
Magnets | 121.03.05 |  | Other |  | LT-SSR1
Vacuum | 121.03.06 |  |  |  | LT-SSR2
Controls | 121.03.07 |  | Floor |  | LT-LB650
SS | 121.03.08 |  | Suspended |  | LT-HB650
Instrumentation | 121.03.09 |  | Rack Mounted |  | LT-Upgrade
WFE | 121.04.02 |  | Beamline/Tunnel |  | LG-General
BldgI | 121.04.03 |  |  |  | LG-HWR
BeamCommissioning | 121.04.04 |  |  |  | LG-SSR1
RingsInst | 121.05.05 |  |  |  | LG-SSR2
BTLBAL | 121.05.04 |  |  |  | LG-LB650
Upgrades | N/A |  |  |  | LG-Upgrade
WBS Names and IDs | Level 2 |  |  |  | LG-HB650
HWR | 121.02 |  |  |  | LG-BTL
SSR | 121.02 |  |  |  | LG-Exterior Space
Elliptical | 121.02 |  |  |  | BTL-Tunnel
CP | 121.02 |  |  |  | BAL-Beam Absorber
CDS | 121.02 |  |  |  | BTL-F3 Building
HPRF | 121.03 |  |  |  | Cryoplant Building
LLRF | 121.03 |  |  |  | UP
Magnets | 121.03 |  |  |  | Booster
Vacuum | 121.03
Controls | 121.03
SS | 121.03
Instrumentation | 121.03
WFE | 121.04
BldgI | 121.04
BeamComissioning | 121.04
RingsInst | 121.05
BTLBAL | 121.05
Upgrades | N/A
Sub-Tier Systems
HPRF | LLRF | Magnets | Vacuum | Controls | SS | Instrumentation | BTLBAL | WFE | BldgI | HWR | SSR | Elliptical | CP | CDS | RingsInst | Upgrades
HB650 | Buncher | Chopper Kicker | WFE | Computers, Center Service | Interlocks | BLM | Collimator Controls | Ion Source | Compressed Air | HWR Cryomodule | SSR1 Cryomodule | LB650 Cryomodule | Cold Box Station | General Data Acquisition |  | RFSep-Cavity
HWR | HB650 | Fast Dipole Switch | HB650 | Computers, Console | Interlocks, SSIU | BPM | RAW Absorber | LEBT | Dissolved Oxygen | Vacuum, Cavity | SSR2 Cryomodule | HB650 Cryomodule | Network Room | HWR |  | RFSep- HPRF
LB650 | HWR | Magnets, C-dipole | HWR | Computers, Front End | ODH | General Instrumentation |  | MEBT | LCW | Vacuum, Insulating |  |  | Warm Compressor Section | SSR1 |  | RFSep-Magnets, Vert. Dip.
MEBT Buncher Cavity | LB650 | Magnets, Dipole | Insulating Vac | Diagnostic Room |  | Laser Wire |  | RFQ | Resistivity Control |  |  |  |  | SSR2 |  | RFSep-Magnets, Lambertson
RFQ | Primary Reference Line | Magnets, Dipole Corrector | Ion Pump PS System | Fiber Distribution |  | MW |  | WFE | Reverse Osmosis |  |  |  |  | LB650 |  | RFSep-Magnets, BLQuads
SSR1 | RF Interlocks | Magnets, Large Bore | SRF | General Data Acquisition |  | MW, Laser Wire |  |  | RFQ |  |  |  |  | HB650 |  | RFSep-Magnets, BLDip.
SSR2 | RFQ | Magnets, Regular Quadrupole | SSR | Laser Transport |  | RWC |  |  | Utility Nitrogen | [6 empty] | RFSep-Spang
| Spare | Magnets, Septum | SSR1 | Motor Controllers |  | Toroid | [9 empty] | RFSep-BLBI
| SSR1 | Magnets, Skew Quadrupole | SSR2 | PLC/LCW Controls |  | Wire Scanner | [9 empty] | RFSep-BLVac
| SSR2 | Magnets, Sweep | LB650 | RAW System
|  |  | RFSeparator | RFQ
|  | Solenoids | BTL/BAL | Timing System
Magnets, Lambertson
Components
HPRF | LLRF | Magnets | Vacuum | Controls | SS | Instrumentation | BTLBAL | WFE | BldgI | HWR | SSR | Elliptical | CP | CDS |  | Upgrades
Cavities | 162.5 LLRF Hardware | Cables | Controller, Ion Pump | Alarms | Critical Device Controller | Laser Room | Magnets | Absorber Assembly | Air Compressor | Couplers | Couplers | Couplers | 4.5K Cold Box | Cryomodule |  | Magnets
Circulators | 325 LLRF Hardware | Magnets | Controller, Ion/Pirani Gauge | Console Computers | Interlock Box | Racks | Power Supplies | Allison Scanner | Bottles | Cryomodule | Cryomodule | Cryomodule | Cold Box Equipment | Racks |  | Power Supplies
Flow Monitors | 650 LLRF Hardware | Power Supplies | Controller, NEG | Consoles, Fixed | Interlock Gates | Racks, Rittal | Pumps | Beamline | Dewar | Pumps and Controllers | Pumps and Controllers | Pumps and Controllers | Compressors | Racks, Rittal |  | Pumps
Interlocks | Power Supplies | Racks | Controller, Turbo Pump | Consoles, Mobile | ODH Monitor | Rack Mount | Racks | Bottle Enclosure | Dryer | Tuners | Tuners | Tuners | Entire Area | Rack Mount |  | Racks
Power Amplifiers | Racks |  | Gauges, Ion | Other Hardware Devices | Racks |  | Racks, Rittal | Bunching Cavities | Filter |  |  |  | Generator |  |  | Power Amplifiers
Power Supplies | Resonance Control |  | Gauges, Pirani | Racks | Racks, Rittal |  | Rack Mount | Cabinets | Heat Exchanger |  |  |  | Panels
Racks |  |  | Power Supplies | Racks, Rittal | Rack Mount |  |  | Chiller | Pump |  |  |  | Skids
Reflected Power Loads |  |  | Pump, Ion |  |  |  |  | Chopper | Skids |  |  |  | Storage Tank
|  |  | Pump, NEG |  |  |  |  | Circulators | Strainer |  |  |  | Welding Receptacle
|  |  | Pump, Roughing |  |  |  |  | Controllers | Tank |  |  |  | Racks
|  |  | Pump, Turbo |  |  |  |  | Couplers | Water/Oil Separator |  |  |  | Racks, Rittal
|  |  | Racks |  |  |  |  | Ion Source |  |  |  |  | Rack Mount
|  |  | Valves, Gate |  |  |  |  | Kickers
|  |  | Valves, Right Angle |  |  |  |  | Magnets
Panels
Power Amplifiers
Power Supplies
Racks | [7 empty] | Racks
Size | Front Access | Closed Sides | Rear |  | Cooling |  |  | Scrapers Vacuum Chamber
Other | Doors | Left AND Right | Closed |  | Air, Compressed |  |  | Skids
* 19"W/52U X 29" D | Open | Left Only | Open |  | Air, Environment |  |  | Solenoids
19"W/60U X 29" D |  | Open | Door |  | Chilled LCW |  |  | Vanes
19"W/42U X 29" D |  | Right Only |  |  | Chilled Water |  |  | Walls
4'W x 6'H x 3'D |  |  |  |  | ICW
TBD |  |  |  |  | LCW
Power to Rack |  | Breaker (A)
120 V - 1 Phase - 2 Wire |  | 15 |  |  | Cable Types
208 V - 1 Phase - 2 Wire |  | 20 |  |  | Flexible <1cm (e.g. RG58)
240 V - 1 Phase - 2 Wire |  | 30 |  |  | "Flexible" >1cm (e.g. 500MCM stranded)
208 V - 3 Phase - 3 Wire |  | 40 |  |  | Semi rigid <1cm (e.g. 0.25" Heliax)
480 V - 3 Phase - 3 Wire |  | 50 |  |  | Semi-rigid >1cm (e.g. 0.5" Heliax)
208Y/120 V - 3 Phase - 4 Wire |  | 60 |  |  | Rigid (e.g. hardline coax)
480Y/277 V - 3 Phase - 4 Wire |  | 120
Other (specify) |  | 125
TBD |  | 200
240
Communication |  | 450
Ethernet |  | Other
ACNET |  | TBD
WIFI
Other (specify) |  | Floors
TBD |  | Bare concrete
Sealed concrete
Disclaimer: | amplifiers at 2mA. CW RF, specify the amplifiers to accelrate 2MW of beam in the cavities