## Slide 1
Ben Hansen, L3/CAM
May 12, 2020
Cryoplant Scope

## Slide 2: Outline
Scope Introduction
Capacity Requirements
Cryoplant Layout and Cryo Interfaces
Summary

## Slide 3: Scope Introduction

## Slide 4: Scope and Deliverables – DAE India
Helium Cryogenic Plant Purchased from Industry
  Coldbox
  Warm Compressor System
Jointly developed Cryoplant specification between DAE/India and Fermilab during BARC SPC long-term visit
Weekly meetings with SPC and 2 long-term visitors from DAE/India at Fermilab.
ESS Coldbox
ESS Compressor Room

## Slide 5: Scope and Deliverables - Fermilab
Services:
  Cryoplant equipment rigging
  Cryoplant Installation
New Equipment:
  Liquid Helium (LHe) Dewar
  Helium Purifier
  Helium Transferline from Coldbox to Dewar
  LN2 Transferline from Dewar to Purifier
  Controls and Instrumentation for Fermilab scope
  Liquid Nitrogen (LN2) Dewar
Existing/Repurposed Equipment:
  Recovery/Purification Compressor
  6x Gas Helium (GHe) Storage Tanks

## Slide 6: Integrated Scope
CP Vendor*
FNAL CryoP
FNAL CF
FNAL CDS
* Vendor work managed by BARC with Fermilab Involvement

## Slide 7: Capacity Requirements

## Slide 8: Cryoplant Capacity Safety Factors
Safety factors, representing the heat load uncertainties and operational overcapacity were explicitly defined to avoid mis-sizing
𝐹𝑆 = 1.3, static heat load safety factor
𝐹𝐷 = 1.1, dynamic heat load safety factor
𝐹𝑂 = 1.05, operational safety factor
Heat Load Summary:
 | 2K (isothermal) | 2K (non-isothermal) | 5K (supply/return) | 40K (supply/return)
CM Dynamic [W] | 1386 | 0 | 146 | 757
CM Static [W] | 203 | 0 | 677 | 3132
CDS [W] | 0 | 258 | 134 | 1971
Total Nominal [W] | 1590 | 258 | 957 | 5860
Total with SF [W] | 1879 | 352 | 1275 | 7839

## Slide 9: Cryoplant Capacity – Requirements
A combined thermodynamic and hydraulic analysis of the CDS and CM system was used to refine the Cryoplant requirements
2K heat load is a combination of isothermal and non-isothermal
The JT Heat Exchanger effectiveness, 2K return flow rate and temperature.
JT Hxer Effectiveness is 0.87 and specification jointly written with SRF CM design group
Charge #1

## Slide 10: Cryoplant Capacity – Requirements
Cryoplant Requirements:
Specified Capacity:
Capacity (W) | 2 K | LTTS | HTTS
Maximum | ≥ 1,900 | ≥ 1,500 | ≥ 9,100
Nominal | ≥ 1,750 | ≥ 1,150 | ≥ 7,000
1879

## Slide 11: Cryoplant Layout and Interfaces

## Slide 12
Cryoplant Building
5/13/2020

## Slide 13: Cryoplant Building Layout
Compressor Station
Coldbox Station
Offices/Commissioning Room
Purification System

## Slide 14: Coldbox Station
CDS Distribution Box
10 kL Dewar
Evap
Coldbox

## Slide 15: CDS Interface
Defining critical interfaces including
  Interface to Coldbox
  Location and envelop size for Distribution Box (DB)
  Location and Window for TL and warm headers exiting Cryoplant Building
Warm headers include LP, GN2 and HP

## Slide 16
PIP-II Cryoplant Interfaces - Controls
5/13/2020
Notes: Cryoplant PLCs interface with CDS PLCs via local ethernet connection and to the Controls via OPC and EPICS

## Slide 17: End