## Slide 1
Andrew Dalesandro and Ram Dhuley
Integrated Cryogenics Workshop Review
14 May 2020
PIP-II Cryogenic System Operating Modes

## Slide 2: Outline
CDS cooldown requirements
CDS HTTS – 80 K Circuit
  Cooldown
  Steady State
  Warmup
CDS LTTS – 5 K Circuit
  Cooldown
  Steady State
  Pumpdown
  Warmup
CDS Steady-State
Note: operating modes and parameters are still in design and development. Specifics presented may be subject to change

## Slide 3: CDS Cooldown - Requirements
During HTTS cooldown/warmup
  Monitor Cryoplant Turbine String 1 temperatures
  Monitor CD Return line pressure and flow rate back to LP Suction
During 5 K circuit cooldown/warmup
  Monitor Cryoplant Turbine String 3 temperatures
  Monitor CD Return line pressure and flow rate back to LP Suction
  Monitor CP liquid dewar pressure and fill level
During 2 K pumpdown
  Monitor CP 2 K liquid level and heater input power
  Monitor cold compressor stability

## Slide 4: CDS Cooldown – HTTS
1. Flow from HTTS Supply in DVB, through CDS HTTS Linac
2. Return flows to CP through cooldown valve in DVB from HTTS Return to CD Return line
1
2

## Slide 5: CDS Steady State – HTTS
Transition to steady-state:
  1. Slowly open DVB HTTS Return valve
  2. Close DVB HTTS cooldown valve
  Regulate CDS HTTS temperature with HTTS Return valve as needed
1
2

## Slide 6: CDS Warmup – HTTS
1. Flow warm gas from HP supply into HTTS at DVB; flow through CDS HTTS Linac
2. Return warm gas flows to CP CD Return using DVB cooldown valve
1
2

## Slide 7: CDS Cooldown – 5 K Circuit
1. Flow from 4.5 K Supply in DVB, through CDS Linac
2. Return flows to CP through cooldown valves in DVB from CDS LTTS Return and 2 K Return circuits
1
2

## Slide 8: CDS Steady State – 5 K Circuit
Transition to steady-state:
  1. Slowly open DVB LTTS Return and 2 K Return valves
  2. Close DVB LTTS Return and 2 K Return cooldown valves
  Regulate CDS LTTS temperature with LTTS Return valve as needed
1
CP
2

## Slide 9: CDS Pumpdown – 2 K Circuit
1. Regulate CDS 2 K Return pressure in Turnaround Can Phase Separator with TC 2 K Return valve
2. Use CDS TC PS ~ 500 W heater to commission 2 K load
CP must compensate ~ 1.5 kW locally to operate CDS at 2 K using CP cold compressors
1
2

## Slide 10: CDS Warmup – 5 K Circuit
1. Flow warm gas from HP supply into 4.5 K Supply at DVB; flow through CDS HTTS Linac
2. Return warm gas flows to CP CD Return using DVB cooldown valve
1
2

## Slide 11: Thank You