## Slide 1
Andrew Dalesandro and Ram Dhuley
Integrated Cryogenics Workshop Review
14 May 2020
PIP-II Cryogenic System Operating Modes

## Slide 2: Outline
CM cooldown requirements and assumptions
CM HTTS – 80 K Circuit
  Slow cooldown
  State-state
  Warmup
CM LTTS – 5 K Circuit
  Slow cooldown
    Option 1
    Option 2
    Option 3
  Fast cooldown
  5 K Fill
  2 K Pumpdown
  Warmup
Note: operating modes and parameters are still in design and development. Specifics presented may be subject to change

## Slide 3: CM Cooldown – Requirements & Assumptions
Slow Cooldown  80 K < T < 300 K
  HWR  no constraints
  SSR1/2  HTTS temperature rate of change ≤ 20 K/hr
  LB/HB650  HTTS temperature rate of change ≤ 20 K/hr
Intermediate Cooldown  45 K < T < 80 K
  No Q-disease requirements for HWR, SSR1/2, or LB/HB650
  No thermal constraints or required cooldown rate
Fast Cooldown  5 K < T < 45 K
  HWR, SSR1/2  no requirement
  LB/HB650  Hold for 1 hour at 45 K
  LB650  ≥ 43 g/s LHe flow through Nb transition temperature
  HB650  ≥ 72 g/s LHe flow through Nb transition temperature
  HWR, SSR1/2  MAWP = 4.1 bara
  LB650  MAWP = 2.05 bara
  HB650  MAWP = 2.05 bara
2 K Pump-down  2 K < T < 5 K
  Single CM or many CMs with 2 K Return nominally at 31 mbar

## Slide 4: CM HTTS - Slow Cooldown
1. Circulate warm gas to establish flow in CM HTTS circuit and vent through HTTS cooldown valve
2. Slowly open HTTS Supply valve
Monitor temperatures and pressures to satisfy CM slow cooldown requirements
Mix warm and cold gas
1
2

## Slide 5: CM HTTS - Steady State
Transition to CM HTTS steady-state:
Slowly open HTTS Return valve in CDS Bayonet Can
Close HTTS Return cooldown valve
Regulate temperature of CM HTTS as needed using HTTS Return valve in BC

## Slide 6: CM HTTS - Warmup
Close CDS BC Supply and Return valves
Open CDS cooldown valve HTTS Return
Slowly open warm supply valves on the HTTS circuit
Circulate warm gas slowly through CM to boil off liquid, and raise temperatures within allowable pressure and temperature limits

## Slide 7: CM 5 K Circuit - Slow Cooldown  Option 1: 4.5 K Supply
Gas flow path during controlled cooldown of cryomodule LTTS and cavities.
Option 1: Use 4.5 K Supply
Pros
  Uses primary supply for CM cavity circuit
Cons
  Does not directly cooldown CM 5 K intercept load or CDS LTTS Return U-tube
  Unclear when to best cooldown 5 K intercept load
  Unclear if fast cooldown can be successful without cooling down 5 K intercept
Mix warm and cold gas

## Slide 8: CM 5 K Circuit - Slow Cooldown  Option 2: LTTS Return
Gas flow path during controlled cooldown of cryomodule LTTS and cavities.
Option 2: Use LTTS Return
Pros
  LTTS Return directly cools CM 5 K intercept
Cons
  Does not directly cooldown CM cavity supply line or CDS 4.5 K Supply U-tube
  Unclear when to begin cooldown of cavity supply line
  Unclear if fast cooldown can be successful through LTTS Return
Mix warm and cold gas

## Slide 9: CM 5 K Circuit - Slow Cooldown  Option 3: 4.5 K Supply and LTTS Return
Gas flow path during controlled cooldown of cryomodule LTTS and cavities.
Option 3: Use both Supply and Return
Pros
  Cool down full CM cavity circuit concurrently
Cons
  Complex: operator must control fours valves and monitor ~ three different temperature readbacks and cavity pressure simultaneously
Mix warm and cold gas

## Slide 10: CM 5 K Circuit - Fast Cooldown
Hold cavity temp. steady at 45 K for 1 hour
With CM cooldown valve throttled, open CDS BC 4.5 K Supply valve
Open CM cooldown quickly, keeping cavity pressure < 2 bara
Once LHe accumulates in cavity helium vessels, transition to 5 K Fill Mode

## Slide 11: CM 5 K Circuit - 5 K Fill Mode
Slowly open CM JT valve
Close CM Cooldown valve
Regulate liquid level with CM JT valve as needed

## Slide 12: CM 2 K Circuit - 2 K Pumpdown
Stabilize cavity LHe level
Close Bayonet Can 2 K cooldown valve
Slowly open BC 2 K Return valve, regulate 2 K LHe bath pressure
Regulate liquid level with CM JT valve as needed

## Slide 13: CM 5 K Circuit - Warmup
Close CM JT valve. Open CM Cooldown Valve
Close CDS BC Supply and Return valves
Open CDS cooldown valve 2 K Return
Slowly open warm supply valves on the 5 K circuit
Circulate warm gas slowly through CM to boil off liquid, and raise temperatures within allowable pressure and temperature limits

## Slide 14: Thank You