## Slide 1: Rack Space Needs for TPC Electronics
Marco Verzocchi
Fermilab
4 June 2020

## Slide 2: Outline
TPC Electronics needs space for
  Low voltage power supplies (power to the warm interface electronics crates, fans, heaters, and related PLC, plus connections between the PTCs and the PLC)
    Description on page 3, repeated 25 times (one per row of APAs)
  Bias voltage supplies (provide high voltage for the APA wires and the field cage electrodes, and related PLC)
    Description on page 4, repeated 5 times (close to rows 3, 8, 13, 18, and 23 of APAs)
  930 Gigabit Ethernet network ports (use 25 48ports Gigabit Ethernet switches, is this sufficient to accommodate the needs also of photon detector system ?)
  Optical fanouts for timing system

## Slide 3: Racks with LV supplies
Space for one WIENER PL506 (4U including fans)
PLC components require 578mm of space (i.e. two DIN rails of 436 mm, there is extra room available in case more power supplies fanouts are needed)
24V supplies for PLC components (also provide power to heaters and fans) may require a 3rd DIN rail
Total of 18U required for the 3 DIN rails, could reduce to 12 U by mounting 24V supplies on the back of a panel
Total 16-22U
1U for network switch
1U for optical fanout of timing system

## Slide 4: Racks with bias voltage supplies
Space for one WIENER MPOD (9U including fans)
Space for patch panels for bias voltage cables (9*1U)
PLC components require 482 mm of space (i.e. two DIN rails, could also fit on a single one but this would be very tight and there wouldn’t be any space for the 24V supply)
Total of 12U required for the 2 DIN rails
Total 21U
Network connection on a different rack

## Slide 5: Total space requirements
LV: 25 times 18U-24U
Bias voltage: 5 times 21U
Total is between 555U and 705U
Old estimate (DocDB 4499) was 400U for LV, bias voltage, supplies for heaters and fans shared with other systems (additional 200U)
Patch panels for bias voltage cables take out space (but consume no power)
  Assume 1U panel with 16 bias voltage connections. CAEN R648 (unsuitable for us because of connections) has 48 connections in 2U (would need 6U total instead of 9 if we can build something with similar density)
  Alternative is to have a sliding shelf with multiple rows of connectors (could fit 32 or 48 connections in 1U ?)