## Sheet1
SBN-ND LAr Circulation from Cryostat Controls Power Analysis
Row 1, Section 1
E-bus | Ref. Des. | Model | Description | Current |  | Power Bus | Ref. Des. | Description | Current
| Term 1 | CX8110 | Embedded PC for EtherCAT, Economy | 375 | mA |  | EV-6002I | 3-way solenoid valve for PV-6002A | 104.1667 | mA
| Term 2 | EL1104 | Digital Input, 24V, 4 Channel | 90 | mA |  | EV-6010I | 3-way solenoid valve for PV-6010A | 104.1667 | mA
| Term 3 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | EV-6011I | 3-way solenoid valve for PV-6011A | 104.1667 | mA
| Term 4 | EL1104 | Digital Input, 24V, 4 Channel | 90 | mA |  | EV-6020I | 3-way solenoid valve for PV-6020A | 104.1667 | mA
| Term 5 | EL1104 | Digital Input, 24V, 4 Channel | 90 | mA |  | EV-6021I | 3-way solenoid valve for PV-6021A | 104.1667 | mA
| Term 6 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | EV-8000I | 3-way solenoid valve for PV-8000A | 104.1667 | mA
| Term 7 | EL1104 | Digital Input, 24V, 4 Channel | 90 | mA |  | EV-8001I | 3-way solenoid valve for PV-8001A | 104.1667 | mA
| Term 8 | EL1104 | Digital Input, 24V, 4 Channel | 90 | mA
| Term 9 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA
| Term 10 | EL1104 | Digital Input, 24V, 4 Channel | 90 | mA
| Term 11 | EL1104 | Digital Input, 24V, 4 Channel | 90 | mA
| Term 12 | EL1104 | Digital Input, 24V, 4 Channel | 90 | mA
| Term 13 | EL1104 | Digital Input, 24V, 4 Channel | 90 | mA
| Term 14 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA
| Subtotal |  |  | 1665 | mA |  | Subtotal |  | 729.1667 | mA
TPC LV Rack (×25) Row 1, Section 1
E-bus | Ref. Des. |  | Description | Current |  | Power Bus | Ref. Des. | Description | Current
| Term x01 | EK1100 | Coupler, EtherCAT | 70 | mA
| Term x02 | EL1004 | Digital Input, 24V, 4 Channel | 90 | mA |  | Fan Readback | (24V / 10kΩ pull-up) × 4 fans | 9.6 | mA
| Term x03 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | Fan Power | (0.33A per fan + 14mA) × 4 fans | 1376 | mA
| Term x04 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | Heaters | ((24V / 68.1Ω) + 14mA) × 4 heaters | 1465.6916 | mA
| Term x05 | EL3202-0010 | RTD Input, 4-wire, 2 Channel | 190 | mA |  | RTDs | 0.5mA × 2 RTDs | 1 | mA
| Term x02 | EL1004 | Digital Input, 24V, 4 Channel | 90 | mA |  | Fan Readback | (24V / 10kΩ pull-up) × 4 fans | 9.6 | mA
| Term x03 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | Fan Power | (0.33A per fan + 14mA) × 4 fans | 1376 | mA
| Term x04 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | Heaters | ((24V / 68.1Ω) + 14mA) × 4 heaters | 1465.6916 | mA
| Term x05 | EL3202-0010 | RTD Input, 4-wire, 2 Channel | 190 | mA |  | RTDs | 0.5mA × 2 RTDs | 1 | mA
| Term x02 | EL1004 | Digital Input, 24V, 4 Channel | 90 | mA |  | Fan Readback | (24V / 10kΩ pull-up) × 4 fans | 9.6 | mA
| Term x03 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | Fan Power | (0.33A per fan + 14mA) × 4 fans | 1376 | mA
| Term x04 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | Heaters | ((24V / 68.1Ω) + 14mA) × 4 heaters | 1465.6916 | mA
| Term x05 | EL3202-0010 | RTD Input, 4-wire, 2 Channel | 190 | mA |  | RTDs | 0.5mA × 2 RTDs | 1 | mA
| Subtotal |  |  | 1630 | mA |  | Subtotal |  | 8556.8749 | mA
TPC LV Rack (×25) Row 1, Section 2
E-bus | Ref. Des. |  | Description | Current |  | Power Bus | Ref. Des. | Description | Current
| Term x01 | EK1100 | Coupler, EtherCAT | 70 | mA
| Term x02 | EL1004 | Digital Input, 24V, 4 Channel | 90 | mA |  | Fan Readback | (24V / 10kΩ pull-up) × 4 fans | 9.6 | mA
| Term x03 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | Fan Power | (0.33A per fan + 14mA) × 4 fans | 1376 | mA
| Term x04 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | Heaters | ((24V / 68.1Ω) + 14mA) × 4 heaters | 1465.6916 | mA
| Term x05 | EL3202-0010 | RTD Input, 4-wire, 2 Channel | 190 | mA |  | RTDs | 0.5mA × 2 RTDs | 1 | mA
| Term x02 | EL1004 | Digital Input, 24V, 4 Channel | 90 | mA |  | Fan Readback | (24V / 10kΩ pull-up) × 4 fans | 9.6 | mA
| Term x03 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | Fan Power | (0.33A per fan + 14mA) × 4 fans | 1376 | mA
| Term x04 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | Heaters | ((24V / 68.1Ω) + 14mA) × 4 heaters | 1465.6916 | mA
| Term x05 | EL3202-0010 | RTD Input, 4-wire, 2 Channel | 190 | mA |  | RTDs | 0.5mA × 2 RTDs | 1 | mA
| Term x02 | EL1004 | Digital Input, 24V, 4 Channel | 90 | mA |  | Fan Readback | (24V / 10kΩ pull-up) × 4 fans | 9.6 | mA
| Term x03 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | Fan Power | (0.33A per fan + 14mA) × 4 fans | 1376 | mA
| Term x04 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | Heaters | ((24V / 68.1Ω) + 14mA) × 4 heaters | 1465.6916 | mA
| Term x05 | EL3202-0010 | RTD Input, 4-wire, 2 Channel | 190 | mA |  | RTDs | 0.5mA × 2 RTDs | 1 | mA
| Subtotal |  |  | 1630 | mA |  | Subtotal |  | 8556.8749 | mA
TPC LV Rack (×25) Row 1, Section 2
E-bus | Ref. Des. |  | Description | Current |  | Power Bus | Ref. Des. | Description | Current
| Term 15 | EL9560 | Power Supply, 24V DC, Isolated | 90 | mA |  | LT-502-N | Level probe for nitrogen in condenser (4-20mA) | 20 | mA
| Term 16 | EL3052 | Analog Input, 4-20mA, 2 Channel | 130 | mA |  | LT-515-Ar | Level probe for argon level in cryostat (4-20mA) | 20 | mA
| Term 17 | EL3052 | Analog Input, 4-20mA, 2 Channel | 130 | mA |  | LT-579-Ar | Level probe for internal filter (4-20mA) | 20 | mA
| Term 18 | EL3202 | RTD Input, 2- or 3-wire, 2 Channel | 190 | mA |  | TE-547-Ar | Temperature sensor (RTD) on filter heater #1 | 0.5 | mA
| Term 19 | EL3202 | RTD Input, 2- or 3-wire, 2 Channel | 190 | mA |  | TE-548-Ar | Temperature sensor (RTD) on filter heater #1 | 0.5 | mA
| Term 20 | EL3202 | RTD Input, 2- or 3-wire, 2 Channel | 190 | mA |  | TE-568-Ar | Temperature sensor (RTD) on filter heater #2 | 0.5 | mA
| Term 21 | EL3202 | RTD Input, 2- or 3-wire, 2 Channel | 190 | mA |  | TE-569-Ar | Temperature sensor (RTD) on filter heater #2 | 0.5 | mA
| Term 22 | EK1110 | Extender, EtherCAT | 130 | mA |  | TE-570-Ar | Temperature sensor on LAr outlet from cond. | 0.5 | mA
[7 empty] | TE-571-Ar | Temperature sensor on LAr outlet from cond. | 0.5 | mA
[7 empty] | TE-581-Ar | Temperature in cryostat vapor space | 0.5 | mA
[7 empty] | TE-582-Ar | Temperature in cryostat under vent entrance | 0.5 | mA
[7 empty] | TE-583-Ar | Temperature at bottom of cryostat | 0.5 | mA
| Subtotal |  |  | 1240 | mA |  | Subtotal |  | 64.5 | mA
Row 2, Section 1
E-bus | Ref. Des. |  | Description | Current |  | Power Bus | Ref. Des. | Description | Current
| Term 23 | EK1100 | Coupler, EtherCAT | 70 | mA |  | DCPS1 | Power Supply, 150V, 16A, 2.4kW (4-20mA × 4) | 80 | mA
| Term 24 | EL3052 | Analog Input, 4-20mA, 2 Channel | 130 | mA |  | DCPS2 | Power Supply, 150V, 5A, 750W (4-20mA × 4) | 80 | mA
| Term 25 | EL3052 | Analog Input, 4-20mA, 2 Channel | 130 | mA
| Term 26 | EL4022 | Analog Output, 4-20mA, 2 Channel | 140 | mA
| Term 27 | EL4022 | Analog Output, 4-20mA, 2 Channel | 140 | mA
| Term 28 | EL2624 | Relay Module, 4 Channel | 200 | mA
| Term 29 | EL9070 | Shield Terminal | 0 | mA
| Term 30 | EL6022 | Serial Interface, RS422/RS485, 2 Channel | 270 | mA
| Subtotal |  |  | 1080 | mA |  | Subtotal |  | 160 | mA
Row 2, Section 2 (5V)
E-bus | Ref. Des. |  | Description | Current |  | Power Bus | Ref. Des. | Description | Current
| Term 31 | EL9505 | Power Supply Terminal, 5V DC | 90 | mA |  | DCPS Interlock | ((5V / 1kΩ load) + 12mA) × 6 channels | 102 | mA
| Term 32 | EL2124 | Digital Input, 5V, 4 Channel | 130 | mA
| Term xx | EL2124 | Digital Output, 5V, 0.5A, 4 Channel | 130 | mA
| Subtotal |  |  | 350 | mA |  | Subtotal |  | 102 | mA
Row 2, Section 3
E-bus | Ref. Des. |  | Description | Current |  | Power Bus | Ref. Des. | Description | Current
| Term 33 | EL9410 | Power Supply, E-bus Refresh | 70 | mA |  | XMTR1 | Temperature / Humidity Transmitter (4-20mA × 2) | 40 | mA
| Term 34 | EL3052 | Analog Input, 4-20mA, 2 Channel | 130 | mA
| Term 35 | EL3202-0010 | RTD Input, 4-wire, 2 Channel | 190 | mA
| Term 36 | EL3202-0010 | RTD Input, 4-wire, 2 Channel | 190 | mA
| Subtotal |  |  | 580 | mA |  | Subtotal |  | 40 | mA
Total
[7 empty] | Total |  | 16.5575 | A
Row 2, Section 4 (12V)
E-bus | Ref. Des. |  | Description | Current |  | Power Bus | Ref. Des. | Description | Current
| Term 37 | EL3681 | Digital Multimeter | 150 | mA |  | RA1 | RTD on heater | 710.1 | mA
| Term 38 | EL9100 | Potential Supply | 0 | mA |  | RA2 | Heater, 16.9Ω | 710.1 | mA
| Term 39 | EL2024-0010 | Digital Output, 12V, 2.0A, 2 Channel | 120 | mA |  | RA3 | Heater, 16.9Ω | 710.1 | mA
| Term 40 | EL1144 | Digital Input, 12V, 4 Channel | 90 | mA |  | RA4 | Heater, 16.9Ω | 710.1 | mA
| Term 41 | EL9011 | End Cap | 0 | mA
| Subtotal |  |  | 360 | mA |  | Subtotal |  | 2840.4 | mA
Total
[7 empty] | Total |  | 2.8404 | A

## TPC LV Rack (×25)
DUNE Detector Safety System - TPC LV Rack (×25) Controls Power Analysis
Row 1, Section 1
E-bus | Ref. Des. |  | Description | Current |  | Power Bus | Ref. Des. | Description | Current
| Term x01 | EK1100 | Coupler, EtherCAT | 70 | mA |  | Fan Readback | (24V / 10kΩ pull-up) × 12 fans | 28.8 | mA
| Term x02 | EL1004 | Digital Input, 24V, 4 Channel | 90 | mA |  | Fan Power | (0.33A per fan + 14mA) × 12 fans | 4128 | mA
| Term x03 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | Heaters | ((24V / 68.1Ω) + 14mA) × 12 heaters | 4397.0749 | mA
| Term x04 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | RTDs | 0.5mA × 6 RTDs | 3 | mA
| Term x05 | EL3202-0010 | RTD Input, 4-wire, 2 Channel | 190 | mA
| Term x06 | EL1004 | Digital Input, 24V, 4 Channel | 90 | mA
| Term x07 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA
| Term x08 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA
| Term x09 | EL3202-0010 | RTD Input, 4-wire, 2 Channel | 190 | mA
| Term x10 | EL1004 | Digital Input, 24V, 4 Channel | 90 | mA
| Term x11 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA
| Term x12 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA
| Term x13 | EL3202-0010 | RTD Input, 4-wire, 2 Channel | 190 | mA
| Subtotal |  |  | 1630 | mA |  | Subtotal |  | 8556.8749 | mA
Row 1, Section 2
E-bus | Ref. Des. |  | Description | Current |  | Power Bus | Ref. Des. | Description | Current
| Term x14 | EL9410 | Power Supply, E-bus Refresh | 70 | mA |  | Fan Readback | (24V / 10kΩ pull-up) × 12 fans | 28.8 | mA
| Term x15 | EL1004 | Digital Input, 24V, 4 Channel | 90 | mA |  | Fan Power | (0.33A per fan + 14mA) × 12 fans | 4128 | mA
| Term x16 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | Heaters | ((24V / 68.1Ω) + 14mA) × 12 heaters | 4397.0749 | mA
| Term x17 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA |  | RTDs | 0.5mA × 6 RTDs | 3 | mA
| Term x18 | EL3202-0010 | RTD Input, 4-wire, 2 Channel | 190 | mA
| Term x19 | EL1004 | Digital Input, 24V, 4 Channel | 90 | mA
| Term x20 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA
| Term x21 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA
| Term x22 | EL3202-0010 | RTD Input, 4-wire, 2 Channel | 190 | mA
| Term x23 | EL1004 | Digital Input, 24V, 4 Channel | 90 | mA
| Term x24 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA
| Term x25 | EL2034 | Digital Output, 24V, 2.0A, 4 Channel | 120 | mA
| Term x26 | EL3202-0010 | RTD Input, 4-wire, 2 Channel | 190 | mA
| Term x27 | EL9011 | End Cap | 0 | mA
| Subtotal |  |  | 1630 | mA |  | Subtotal |  | 8556.8749 | mA
Row 1, Section 3 (5V)
E-bus | Ref. Des. |  | Description | Current |  | Power Bus | Ref. Des. | Description | Current
| Term x36 | EL9505 | Power Supply Terminal, 5V DC | 90 | mA |  | DCPS Interlock | ((5V / 1kΩ load) + 12mA) × 6 channels | 102 | mA
| Term x37 | EL2124 | Digital Output, 5V, 0.5A, 4 Channel | 130 | mA
| Term x38 | EL2124 | Digital Output, 5V, 0.5A, 4 Channel | 130 | mA
| Term x39 | EL9011 | End Cap | 0 | mA
| Subtotal |  |  | 350 | mA |  | Subtotal |  | 102 | mA
Row 2, Section 1
E-bus | Ref. Des. |  | Description | Current |  | Power Bus | Ref. Des. | Description | Current
| Term x28 | EK1100 | Coupler, EtherCAT | 70 | mA
| Term x29 | EK1521 | Fibre Optic Junction, EtherCAT, 1 Channel | 350 | mA
| Term x30 | EK1521 | Fibre Optic Junction, EtherCAT, 1 Channel | 350 | mA
| Term x31 | EK1521 | Fibre Optic Junction, EtherCAT, 1 Channel | 350 | mA
| Subtotal |  |  | 1120 | mA |  | Subtotal |  | 0 | mA
Row 2, Section 2
E-bus | Ref. Des. |  | Description | Current |  | Power Bus | Ref. Des. | Description | Current
| Term x32 | EL9410 | Power Supply, E-bus Refresh | 70 | mA
| Term x33 | EK1521 | Fibre Optic Junction, EtherCAT, 1 Channel | 350 | mA
| Term x34 | EK1521 | Fibre Optic Junction, EtherCAT, 1 Channel | 350 | mA
| Term x35 | EK1521 | Fibre Optic Junction, EtherCAT, 1 Channel | 350 | mA
| Subtotal |  |  | 1120 | mA |  | Subtotal |  | 0 | mA
[7 empty] | Total |  | 23.0657 | A