## Slide 1
Ryan Crawford
Preliminary Design Review
August 31, 2020
Building Infrastructure Electrical PDR

## Slide 2: Outline – Part 1
AC Distribution
  System Requirements
  CF Infrastructure Scope
  Linac Installation and Building Infrastructure Scope
  Safety
Cable Plant
  Documentation
  Cable Counts
  Pull Plans
  Cable DB
  QC
  Risks

## Slide 3: Outline – Part 2
Racks
  Requirements
  CF Space Planning
  Current Design
  Path Forward
Lessons Learned
  LCLS-II (SLAC)
  FRIB
  PIP2IT

## Slide 4: AC Distribution - Requirements
System Requirements captured in RDS
  Controlled document in TeamCenter
F-121.04.04-A012
F-121.04.04-A013

## Slide 5: AC Distribution - Requirements
RDS Captures
  Voltage, Current, PF, Single or Three Phase
  Filtering Requirements
  Backup Power requirements
Follow NEC code
  NRTL ratings
  Sizing
  Keep clear areas
FESHM
F-121.04.04-A012

## Slide 6: AC Distribution – CF Infrastructure Scope
Unit Sub Stations
  3 MVA transformers with dual 1500 kVA secondaries in most cases
    Design allows for phase shifting if necessary
    Dry-Type
  2x 2000A secondary breakers (LSIG protection) in most cases
  Transformers that feed Amplifiers are connected via two motorized disconnect switches
    Kirk Key
    Allows for easy tunnel access
    Amplifier controls powered via second feed
      No interruption to controls work during access
  Underground cable entry, Overhead cable way exit
F-121.04.04-A012

## Slide 7: AC Distribution – CF Infrastructure Scope
F-121.04.04-A012

## Slide 8: AC Distribution – CF Infrastructure Scope
208Y/120V Feeds
  Most systems fed via Busway or Wireway with an occasional conduit fed system
  Feeds sized from RDS and Rack Bank Sheet
  Easily Expandable
  Minimal Spares
  Consistent approach
    All feeds 3 Phase?
F-121.04.04-A012
F-121.04.04-A013

## Slide 9: AC Distribution – CF Infrastructure Scope
480Y/277V Feeds
  Most systems fed via Busway or Wireway with an occasional conduit fed system
    Power Supplies fed via Conduit
  Feeds sized from RDS and Rack Bank Sheet
    RDS Indicators added to CF drawings
  Easily Expandable
F-121.04.04-A012

## Slide 10: AC Distribution – CF Infrastructure Scope
Cable Tray
  All Cable Tray is provided by CF prior to Beneficial Occupancy
  Multiple Levels along East Wall
F-121.04.04-A018

## Slide 11: AC Distribution – CF Infrastructure Scope
Ground
  CF will provide a building ground
  500 MCM ground will be available the entire length of the tunnel
F-121.04.04-A014

## Slide 12: AC Distribution – LI/BldgI Infrastructure Scope
Relay Racks
  LI will manage plug and cord connections of relay racks, and 480V conduit and THHN feeds as necessary from the load side of the disconnect switch
    Wireway will be used when necessary to minimize costs, but will be managed in the same way as busway
F-121.04.04-A012

## Slide 13: AC Distribution – LI/BldgI Infrastructure Scope
Amplifiers
  LI will install conduit/liquid-tight and THHN for amplifier loads from the load side of the disconnect switch
F-121.04.04-A012

## Slide 14: AC Distribution – LI/BldgI Infrastructure Scope
Ground
  LI will attach grounding material provided by BldgI to the main CF trunk line
  Any equipment likely to become energized must be grounded
  Verify that grounds maintain metal to metal contact
CF Scope
BldgI and LI
Scope
F-121.04.04-A014
F-121.04.04-A020

## Slide 15: AC Distribution – Safety
LOTO
  208Y/120V systems are almost exclusively plug and cord
    Voltage indicators still in use at the termination box of the busway
  480Y/277V systems will have voltage indicator and test points
Grounds
  All cable tray grounds must be visible and easily traced back to building ground
F-121.04.04-A012
F-121.04.04-A014

## Slide 16: Cable Plant – Documentation
PIP-II-DocDB-2892: Cable Pull and Documentation Plan
  Overall cable plant management document
  Roles and responsibilities
  Schedules
PIP-II-DocDB-2824: Standard Cable and Connectors
  Formally lists material Building Infrastructure will purchase for L3 systems
  Based on input from L3 systems
PIP-II-DocDB-3054: Cable Criteria
  Formalizes cable requirements
PIP-II-DocDB-4900: Cable Scaling
  Explains methodology behind current cable counts
F-121.04.04-A016

## Slide 17: Cable Plant – Cable/Pull and Documentation Plan
Cable DB Design and Entry Phase Responsibilities
  L2Ms
    Oversee DB design and L3 entries
  L3Ms
    Beta testers
    Responsible party for cable entries
  Cable Coordinator
    Involved at every stage
    Manages Cable DB
  Technical Integration Team
    Manages cable/cable DB issues that span multiple systems
F-121.04.04-A016

## Slide 18: Cable Plant – Cable Pull/Documentation Plan
Installation and Validation Phase
  Technical Integration Team
    Manages Installation or QC issues that span multiple systems
    Track progress
  Installation L2M
    Review weekly roll up reports
    Oversee Installation L3M
      Assume duties if L3M unavailable
  Installation L3M
    Manages Installation
    Review weekly roll up report
    Alert TM/CC and Cable Coordinator if any issues arise
    Assume Cable Coordinator role if they are unavailable
F-121.04.04-A016

## Slide 19: Cable Plant – Cable Pull/Documentation Plan
Installation and Validation Phase
  TM/CC
    Manage contract electricians
    Present issues to Cable Coordinator and Installation L3M
  Contract Electricians
    Responsible for cable pulls
    Temporary labeling
    Terminate load and network cables
    Produce field markup drawings
  L3Ms
    Validate cable pulls
    Present issues to Installation L3M, Cable Coordinator, and TM/CC
F-121.04.04-A016

## Slide 20: Cable Plant – Cable Pull/Documentation Plan
Installation and Validation Phase
  Sub System Engineer
    Validate Cable Pulls
    Alert L3M, TM/CC, Cable Coordinator of any issues
    Manage technicians
      Terminate cables
      Label cables
  Cable Coordinator
    Hold weekly meetings with TI group
    Single Point Contact for Cable DB
    Provide weekly roll up reports
    Print and deliver permanent cable labels
    Perform QC checks at delivery
    Document QC checks
    Release material to Installation L3M
    Provide training
F-121.04.04-A016

## Slide 21: Cable Plant – Cable Pull/Documentation Plan
Schedule
  Request more cable and connector information at 60% CF drawing milestone
    Reevaluate tray fill
    Reevaluate penetration fill
  Finalize cable and connector types by CF 90% drawings
F-121.04.04-A016

## Slide 22: Cable Plant – Standard Cable/Connectors
Cable
  Tracks common cable types
    L3M input
    PIP2IT
  Provides link to datasheets
  Cable not shown in this document is considered “special”
Connectors
  Track common connectors
    Only show one “gender” and/or type
      Need to expand
  Provides link to datasheets
F-121.04.04-A016

## Slide 23: Cable Plant – Cable Criteria
Ratings
  Presents NEC guidelines and references
    Ampacity
    Voltage
    Tray Rating
    UV Rating
    Vertical Flame Tests
    Connector Ratings
  Fermilab Requirements
    Color Code
    Low Smoke Zero Halogen
F-121.04.04-A016

## Slide 24: Cable Plant – Cable Scaling
Methodology
  Based on CMTF Cable DB
    Need to validate against PIP2IT now that all cables are pulled for HWR and SSR1 prototype
Location | Count | Comments
PIP2IT WFE | 752 | CMTF Cable DB
CMTS1 | 884 | CMTF Cable DB
Location | Count | Comments
Scaled PIP2 | 17,825 | Total Count: 19,411
Super conducting LINAC Power Cables | 309 | 
BTL Signal Cables | 1,145 | 
BTL Power Cables | 132 | 
Location | Count | Comments
BOE Signal Cables | 19,221 | Per CD-2 Total Count: 19,662
BOE Power Cable Count | 441 | Per CD-2
F-121.04.04-A016
F-121.04.04-A018

## Slide 25: Break

## Slide 26: Cable Plant – Pull Plans
Tray
  Sensitive equipment is located nearest to the tunnel entrance
  3 levels
    Power, Clean Signal, General Signal
  Minimize long runs by locating equipment in gallery near the equipment it feeds in the tunnel
  Tray will be installed with a cantilever support
    Trapezes will be used only where necessary
  Label all sections of tray for easy tracking
Develop and track weekly pull plans in Cable DB
    Everyone involved has real time updates
    Write privileges limited to Installation L3M, Cable Coordinator and TM/CC
F-121.04.04-A018

## Slide 27: Cable Plant – Pull Plans
Tray Sizing
  Spreadsheet developed
    Checks NEC requirements based on tray usage
      For instance : power cable may only allow for width of the tray and % fill plays no role
    Based on BOE counts
    Alerts if 20% overhead is not maintained
    Can account for different tray sizes and automatically adjusts
    Can account for control fiber Panduit
      Uses 4” of available tray width
    Checks and tracks weight per linear foot
F-121.04.04-A018

## Slide 28: Cable Plant – Pull Plans
Tray Sizing
  Different sheet for each cryomodule section and the BTL
    BTL currently presents problems, but building F37 will elevate many if not all tray concerns
F-121.04.04-A018

## Slide 29: Cable Plant – Pull Plans
Penetration Sizing
  Handled in much the same way as tray
    Power cables must be de-rated manually
      Hoping to account for this soon
F-121.04.04-A018

## Slide 30: Cable Plant – Pull Plans
Penetration Heating
  Using ETAP to minimize inadvertent heating issues
    Heating from power supply cables may be problematic for LLRF
F-121.04.04-A018

## Slide 31: Cable Plant – Cable DB
F-121.04.04-A015

## Slide 32: Cable Plant – Cable DB
List
  Track approvals, status, type, origin, destination, route
  Search entire database
F-121.04.04-A015

## Slide 33: Cable Plant – Cable DB
New Entry
  Allows users to add information to the DB
F-121.04.04-A015

## Slide 34: Cable Plant – Cable DB
Dashboard
  Real time graphs for important information
F-121.04.04-A015

## Slide 35: Cable Plant – Cable DB
Batch Tracking
  Lock out dates
  Procurement tracking
F-121.04.04-A015

## Slide 36: Cable Plant – Cable DB
Pull Planner
  Allows for pull plans that are accessible by everyone
  Real time updates
    Everyone works from the same information
F-121.04.04-A015

## Slide 37: Cable Plant – Cable DB
Report Builder
  Allows for quick weekly roll up reports
  Allows for custom reports
F-121.04.04-A015

## Slide 38: Cable Plant – QC
Delivery
  Cables
    Visual inspection with two individuals
    Continuity check with length meter or multimeter
    Validate part numbers against PO
    Validate lengths against PO
  Connectors
    Visual inspection with two individuals
    Validate part numbers against PO
    Validate count against PO
    Only check a certain % in each package, but inspect every package
Installation
  Multiple checks of pulled cable
    Both Fermilab and Contractor Checks
    Single Point contacts provided for quick issue resolution
F-121.04.04-A016

## Slide 39: Cable Plant – QC
Travelers
  Being developed for Cable, Connectors, Racks
Master Tracking Spreadsheet
  Tracks PO’s, Inspections, Travelers, Status, etc.
Building Infrastructure Materials QC Plan
  QC Plan drafted and submitted for peer review
  Adheres to Linac Installation & Commissioning QA Plan (PIP-II-doc-2611)
F-121.04.04-A016
F-121.04.04-A017

## Slide 40: Cable Plant – Risks
Long Lead Times
  Lots of time built into schedule
  Cable DB tracks cables that may be problematic
Installation issues
  Allow for flexible pull plans
  Everyone works from a database that is updated constantly
  Single point contacts for quick resolutions
Material Damage
  Schedule allows for time to replace damaged cable
  Strong QC plan will be crucial to minimize disruptions due to material damage
  Cable will be stored near installation site to minimize transportation risks on site
F-121.04.04-A016

## Slide 41: Racks – Requirements
RDS Captures Requirements
  Quantity
  Power requirements
  Filtering requirements
  Water requirements
  System owners
  Space requirements
Independent Rack Layout Worksheet (Next Slide)
  Used to validate RDS entries
  Individual systems are responsible for populating
  Managed by Cable Coordinator
F-121.04.04-A012
F-121.04.04-A013

## Slide 42: Racks – Requirements
Rack layout worksheet
  Used to validate rack counts, location, and power draws
  Coded alerts to flag possible problems or issues that need review
    End-rack required?
    Multiple power sources
    Liquid cooling
    Proximity requirements
    Any other special concerns
Front rack view
Total rack power requirement
Rear rack view
Title block
F-121.04.04-A012
F-121.04.04-A013

## Slide 43: Racks – CF Space Requirements
Space Allocation Meeting
  Weekly meeting between multiple L3 systems to discuss space requirements
  LI group builds a 3D model based on these meetings and passes this information to the CF A/E firms
Group Meetings
  Will be used to allocate rack space
    Location requirements
    Space sharing concerns
  Each L3 system will be able to review and comment on applicability for their system
Current Allocation
  First pass complete based on information from L3 systems
  Information was used to form Rack Bank tracking spreadsheet
    Relates every rack requirement back to the RDS
F-121.04.04-A012
F-121.04.04-A013

## Slide 44: Racks – CF Space Requirements
LI Model
  Used to layout space based on RDS
  Information passed to A/E Firms
F-121.04.04-A012
F-121.04.04-A013

## Slide 45: Racks – CF Space Requirements
Rack Bank Spreadsheet
  Linked back to LI Model
  Will be used to allocate space moving forward
F-121.04.04-A012
F-121.04.04-A013

## Slide 46: Racks – Current Design
Rack Specification
  In process
    52 RMU
    Tool-less, plated, and marked support rails
    Support Shelves
    Top, Bottom, Rear, and Side Panels
    Heavy-Duty construction with transportation pallet
    Grounding and Bonding Requirements
    LED Lighting
    Ganging Kits
    PDU Mounting Rail
    Cable management
F-121.04.04-A017

## Slide 47: Racks – Current Design
F-121.04.04-A017

## Slide 48: Racks – Current Design
F-121.04.04-A017

## Slide 49: Racks – Current Design
F-121.04.04-A017

## Slide 50: Racks – Path Forward
Rack Working Group
  Receiving input and specification assistance from multiple systems
    LLRF
    Instrumentation
    Power Supplies
    Controls
  Purchase a prototype rack
    Allow system users to provide feedback
    Modify specification
F-121.04.04-A017

## Slide 51: Racks – Path Forward
Consider new Filtered PDU
    Allows for 3 phase power in, custom outputs
    Filtered
    Individually protected outlets on the front
      Minimize accidental trips from test equipment, cleaning crews, etc.
    Allows for recessed installation for added protection
*Image from Marway Power Solutions
PDU datasheet
F-121.04.04-A017

## Slide 52: Lessons Learned - SLAC
Cables must have an owner that is outside of the A/E Company
  Cable Coordinator is responsible for the cable plant
  Fermilab has oversight capabilities and responsibilities for QC
Fully Integrate with CF
  Cable Coordinator is involved with CF via weekly meetings
  Cable Coordinator holds smaller meetings with system owners
Manage Cable DB continuously
  Cable DB is real time
  Allow for plan routing of cables
3D models early on
  A/E is developing a 3D model with input from LI L3M
  Managed via weekly space allocation meetings

## Slide 53: Lessons Learned - FRIB
Contractor only received copy of DB once a month
  Real time Cable DB
    Contractors will have Read and “Mark as Pulled” capabilities
Let Contractor purchase and manage cables
  Exploring this option
    Fermilab oversight is a must
    Schedules must be developed with input from multiple individuals
      LI L3M
      LI L2M
      Contractor
Give contractor cable information up front
  Crafted a standard cable and connector document
  Will provide special cable information when needed

## Slide 54: Lessons Learned – PIP2IT
Maintain consistent labeling
  Added scope to account for cable labeling
  Names must be agreed upon early
    Minimize/Eliminate name changes when installation is occurring
Consider having individual pulls cut to length
  This has worked well across the laboratory
    Currently evaluating vs. bulk spooling