## Slide 1
Controls Working Group: Summary
Jim Patrick + Elvin Harms / Fermilab
PIP-II Technical Workshop
04 December 2020

## Slide 2: Controls Working Group: Agenda Overview
Overview of the PIP-II control system
Common Hardware Platform discussion
Modern EPICS standards
Front-end/IOC standards
Controls hardware overview
RF interfaces to the control system
Instrumentation interfaces to the control system
PIP-II timing system
Software infrastructure and code management
Round table discussion with partners
  Experiences and lessons learned with migration, collaboration
Many excellent presentations!

## Slide 3: Control System Overview Summary
The PIP-II Control System will be based on EPICS
A parallel project, ACORN, will upgrade the existing complex to EPICS
  Unified control system by the time of booster injection from PIP-II
We are in the early planning phases of the detailed implementation
  And so do not currently have detailed standards for partners
We plan to leverage development and experience from recent accelerator projects
We plan to use modern features in EPICS – EPICS 7 and recent tools
We plan to contribute to future developments in EPICS to meet our requirements
The cryomodule test stand in 2022 will be the first full EPICS implementation
The system will be scaled up during beam commissioning

## Slide 4: Common Platform + Instrumentation Interface (Drennan/Diamond) Front-end/IOC standards (Nicklaus)
Standard platforms provide engineered elements to reliable systems.
  Initial cost savings
  Commercially available hardware
Common Components
  Reduced manpower both initially and into the life of the system.
Fermilab has been investigating microTCA
  Still much to learn
Also has built network attached devices
No plans for future VME development

## Slide 6: Fermilab Direction
Summary
  Linux is replacing VxWorks as an embedded OS
    Hard real-time requirements are being pushed into the FPGA
  We’re converging on a common EPICS IOC platform
  The path beyond VME is becoming more clear
    Gigabit ethernet is replacing the VME bus for data acquisition
      DDCP is a maturing, lightweight UDP protocol for communicating with ethernet-attached devices
      Need to look at DPDK to eliminate the network-stack bottleneck
    MicroTCA favored for high channel density systems
    SoC FPGAs are affordable alternatives for low channel density
  Replacing SBCs with commodity x86 server PCs and ARM SoCs is an affordable way to scale up CPU resources

## Slide 7: Front-end IOC Standards - Minimum
Easily reconfigurable — e.g. we change your name prefix to match our standards and instances.
Locally rebuildable from source code
Adhere to our (TBD) standards (EPICS base version, ...) and protocols
Fit into our deployment plans
Test Suites So…
We need to publish our standards
Describe our database integration plans
Publish guidelines
PLCs — there are no plans to distribute a standard PLC hardware and software bundle. But there should be some thought/agreement here

## Slide 8
Dalesio - Osprey

## Slide 10: Hardware Overview (Kucera)
PLC based controls for
  Vacuum gauges, pumps, valves, …
  Beamline and cryo insulating vacuum
  Cryo delivery system (PLCs responsibility of cryo)
  Cooling water
General Data Acquisition
  HRM-II – 64 10KHz ADCs, 8 16 bit DACs, 8 bytes digital I/O, 8 programmable triggers
  Used for power supply control and monitoring at PIP2IT
Motion control
  Cavity tuners, scrapers, instrumentation, collimators
  Commercial hardware, currently VME based front-end

## Slide 11
325 MHz SSA interface – Manjiri Pande

## Slide 13
650 MHz SSA interface - Lad

## Slide 14: PIP-II Timing System (Austin)
The PIP-II timing system is planned to be a two-part system
The first part is a global timing system (here called ACLK) that provides high level, event based timing for the whole Fermilab accelerator complex
The second part is a RF synchronized clock system unique to the PIP-II linac itself (here called LCLK-II)
The ACLK system will be clocked at 650 MHz. A frame consists of the following:
65 bits total frame |  | 0 | MSB |  | LSB | MSB |  | LSB | X | 111111111111111
 |  | start bit |  | 16-bit EVENT |  |  | 32-bit Data |  | Parity bit | Pad bits # 51-65
The LCLK-II system will be clocked at 650 MHz. A frame consists of the following:
52 bits total frame |  | 0 | MSB |  | LSB | MSB |  | LSB | X | 1 | 1
 |  | start bit |  | 16-bit EVENT |  |  | 32-bit Data |  | Parity bit | pad bit | pad bit
Data field may be time or cycle stamp to correlate data, or fast data needed by the front-end

## Slide 15: PIP-II Timing System Block Diagram

## Slide 16: PIP-II Software Organization (Levshina)
The development of the software for the PIP-II will take several years.
The maintenance of the PIP-II software will take many years.
There are multiple developers and multiple organizations with different approaches for software development and different organizational rules.
That is why it is crucial to figure out how we want to structure a project, so it is possible to
  Understand the layout and dependencies
  Understand the purpose of a particular subproject/module
  Avoid duplication of development efforts and promote reuse
  Decide on branching/tagging and release procedure

## Slide 17: Fermilab Version Control Platform Roadmap
Recent code development has used a Fermilab git implementation - Redmine
Strong push to use GitHub for the future
Fermilab developers could contribute code to public GitHub Open-Source projects
  Needs approval from Fermilab Intellectual Property Management team
The Core Computing Division supports GitHub Enterprise on-Prem. They are running PIP-II IT instance with 20 licenses
  This allows private repositories
  Some testing of Continuous Integration has been done
The Scientific Computing Division has some experience with GitLab on-site.

## Slide 18: Invited Roundtable Panel Members
Gopal Joshi, Sandeep Bharade, Radhika Nasery - BARC
Julien Branlard – DESY/XFEL & FAST
Wojtek Cichalewski – Lodz University of Technology-DMCS/ESS
Graham Cox – STFC Daresbury Laboratory
Krzysztof Czuba – Warsaw University of Technology/ESS
Françoise Gougnaud & Paul Lotrus – CEA Irfu
Many excellent presentations on short notice – Thanks!

## Slide 19: Opening Questions for Panel
To conclude this week's PIP-II Technical Workshop/Controls working group we intend to have a round table discussion on international experience with Controls. To start the conversation our panel members are asked to consider the following:
Notable ‘Lessons Learned’ with respect to controls
Best practices in Controls design/implementation
Controls migration experience
What requirements did you get/not get (and should have) for previous controls projects?
What languages and frameworks have you used for writing user applications?
optional: - git repository structure: what products have you used; what are their differences?
- experience with uTCA

## Slide 20: Lessons Learned
Naming convention is valuable, not just for controls variable names but extending that to engineering drawings etc.
  This has been done for PIP-II!
  As designs progress, anticipate that the naming convention may need to evolve
  Tools for flagging invalid names can be useful. Straightforward for controls names
MicroTCA is broadly used
  Implementations vary in detail
  Fermilab instrumentation proposal is different than what is done elsewhere
  Ethernet with custom protocols
Interfaces should be discussed and agreed upon early in the design process
  There may be unexpected interfaces as design matures
  And requirements and detailed specifications should be shared as soon as available

## Slide 21: Open Issues
Detailed planning for the full PIP-II system is currently in the early phases
Supported hardware platforms
  MTCA – details – data transfer method etc.
  Common general purpose boards?
  VME discouraged?
Timing system integration – receiver boards, FPGA logic
IOC/front-end standards for
  Supported platforms, operating systems
  EPICS version and code, database structure
Application languages and frameworks
Code management system and code structure

## Slide 22: Controls Working Group: Conclusions
Very productive meeting and worth repeating in ~6 months
11+ talks + roundtable discussion w/presentations
Average attendance ~50 people/day. Peak > 60 – many more than expected!
Detailed planning of the EPICS control system for PIP-II is beginning
We plan to learn from other labs as we do this
The first full EPICS system will be the cryomodule test stand
The system will be scaled up during beam commissioning
We are working with microTCA and would like to develop common platforms
Good communication with our international partners is essential at an early stage