## Slide 1: Decay Region Construction and Operation Geometry
Beam Interface Working Group
Jonathan Lewis
19 November 2020

## Slide 2: Overall Design
The project has adopted the “box in a box” design
  Decay vessel shielding is contained within an outer concrete structure
    Barrier to water ex- and infiltration
    Allows for inspection
Nitrogen Gas Cooling Channel
Nitrogen Return

## Slide 3: Thermal Expansion
Energy Deposition results used in thermal FEA
  Temperature 60C for 2.4MW operation
  Shows expansion of 5-8cm along 200m length
  Single cooling return pipe causes lateral distortion
    Will revert to design left-right symmetry

## Slide 4: Construction Features
Structure is locked to base slab at top
  Expansion is toward absorber hall
  Avoids displacement of target
Locked to foundation
Sliding on base slab
Slab on piers that rest on bedrock
Slab on bedrock

## Slide 5: Absorber Moves with Decay Pipe
The arrangement solves many structural and cooling problems
Decay region length will change depending on decay pipe heating
  Should reach a steady state after a few weeks of operation
  Have access to top of decay structure, so this can be measured
Absorber
Slip Plane
Measure Here?

## Slide 6: Construction Process
Start with a massive excavation
Then build the base slab

## Slide 7: Construction of Decay Structure
Build in sections
  Concrete set in a series of 5-foot lifts
  Add sections of pipe as you go along
  Pipe set with typical construction tolerances: ~1/4 inch
Add outer structure
Fill in excavation

## Slide 8: Concerns and Questions
Pipe position will be set by survey crew as it is built
  Will check for residual magnetic fields after welding
  Will sink ~1 inch after structure is complete and excavation is filled
    Awaiting calculations for current design
Not a perfect cylinder
  Some amount of wiggle expected
  1-2 cm out of round with axis varying over length of pipe
How concentric does the pipe need to be with beamline?
  Do we need to compensate for expected movement when it is placed?
How well does position need to be measured?
  In principle can get mm accuracy from Alignment staff
  Is measurement required after settlement is expected to be complete?
  Could we measure the outside of the structure to before and after to look for settlement?
How well do we need to measure elongation?

## Slide 9: Backup

## Slide 10: Construction of Decay Structure
Build in sections
  Concrete set in a series of 5-foot lifts
  Add sections of pipe as you go along
  Pipe set with typical construction tolerances: ~1/4 inch
Add outer structure
Fill in excavation