## Slide 1
HB650 Test Stand – Cryogenic System
Joe Hurd, Ben Hansen, Renzhuo Wang
April 15, 2021

## Slide 2: Outline
Functional Requirements
Special Modes of Operation
CTL Design
Relief Header Modifications
Fast Cooldown Preliminary Analysis

## Slide 3: Special Modes of Operation
Thermal Bump to 45K
Fast Cooldown
Heat Load Measurements
  HTTS
  LTTS
  2K Static/Dynamic

## Slide 4: 650 Test Stand FRS ED0013603 Key Requirements
Independent cryogenic operations from CMTS
Independent cryogenic operations for SSR cryomodules.
Repattern HWR bayonet locations to match 650 bayonet locations
HTTS controlled cooldown/warm up at 20K/hr
  Installation of warm supply required
50K thermal bump on cavities
Maintain LTTS around 5K during thermal bump
Fast cooldown required estimated 80-100g/s
2K operations capable.
Static heat load measurements
  High Temperature Thermal Shield
  Low Temperature Thermal Shield
  Cavity 2K bath
Red text = not capable for on current as built PIP2-IT cryo distribution system

## Slide 5
FT2
Kinney WVC
FT1
HT
FCI Thermal flow meter used to measure CM CD return flows at room temperature
FT1 is a 0-5 g/s model for measure 2K heat loads
FT2 is a large range 0-80 g/s with dual sensing elements for consistent accuracy across full range
FT2 is used to measure Fast Cooldown flow rate and LTTS and HTTS heat loads measurement
Simplified Process Flow Diagram of Integrated System
PV-FCD

## Slide 6
FT2
Kinney WVC
FT1
HT
~60 g/s
~60 g/s
HP Supply
1200 W
Fast Cooldown Step 1 – Thermal Bump to 45K
HP supply gas is used to mix with 4.5K gas to regulate the cavity supply temp to 45K and soak for >30min.
LTTS reverse flowed with trickle of 4.5K gas to keep intercepts cold.
Cryoplant refrigeration of ~1200W regulated in external dewar and reserve liquid accumulated
Fast CD return is through a DN80 valve off the relief stack of the CM.
T

## Slide 7
FT2
Kinney WVC
FT1
HT
60 g/s
~60-80 g/s
HP Supply
1200 W
~60-80 g/s max
Fast cooldown is initiated by fixing the external dewar heater at ~1200W
HP mixing valve is closed
LTTS reverse flow closed
External dewar supply is ramped closed while the CM CD valve ramped open
FT2 will measure the full fast cooldown flow rate until liquid begin accumulating at which point it will drop off

## Slide 8
FT2
Kinney WVC
FT1
HT
HP Supply
HTTS Heat Load Measurement Configuration
To
Ti
HTTS Static heat load is measured by returning only the HTTS flow to CD line to measure flow rate.
The heat load is then calculated based on change in enthalpy times mass flow rate.

## Slide 9
FT2
Kinney WVC
FT1
HT
HP Supply
LTTS Heat Load Measurement Configuration
To
Ti
LTTS Static heat load is measured by returning only the LTTS to the CD line to measure its flow rate.
The heat load is then calculated based on change in enthalpy times mass flow rate.

## Slide 10
FT
Kinney WVC
FT
HT
HP Supply
Cavity Heat Load Measurement Configuration
Ti
Pi
2K flow rate is measured with FCI thermal flow meter FT1 at outlet of the Warm Vacuum Compressors
The heat load is then back calculated from this flow rate and the JT expansion properties.

## Slide 11: Heat load Measurements - Instrumentation
Circuit | Measurement | Tag # | Sensor | Range | Description/Location
HTTS | Temperature Inlet | TX-035 (A/B) | Lakeshore PT-103 Platinum RTD | 14K-873K | On HB60 HTTS Inlet: Side port
 | Temperature outlet | TX-036 (A/B) | Lakeshore PT-103 Platinum RTD | 14K-873K | On HB650 HTTS Outlet: Side port
 | Pressure Inlet | PT-607-H | Sentra # 2061500PG2M11T18NN | 0-500 psig | On PIP2-IT Transfer line
 | Pressure Outlet | PT-608-H | Sentra # 2061500PG2M11T18NN | 0-500 psig | On PIP2-IT Transfer line
LTTS | Temperature Inlet | TX-030 | Cernox | 1.4K -325K | On HB60 HTTS Inlet: Side port
 | Temperature outlet | TX-034 | Cernox | 1.4K -325K | On HB650 HTTS Outlet: Side port
 | Pressure Inlet | PT-605-H | Sentra # 2061500PG2M11T18NN | 0-500 psig | On PIP2-IT Transfer line
 | Pressure Outlet | PT-606-H | Sentra # 2061500PG2M11T18NN | 0-500 psig | On PIP2-IT Transfer line
HTTS & LTTS1 | Flow Meter | FT-601-H | FCI ST100A: Split Range Thermal Mass flow meter | Analog 1: 0-20 g/s Analog 2: 20-200g/s | Suction Header near SCP plant
2K | JT Heat exchanger Temperature inlet | TX-032 (A/B) | Cernox | 2K -325K | HB650 inlet: Sideport
 | Helium Vessel Pressure | PT-041-H | MKS 230EA–00100BB | 0-100 Torr | Helium vessel 2phase Pipe
 | Flow Meter | FT-K2K3SUM | FCI: ST80: Thermal Mass flow meter | 0-15 g/s | Kinney Vacuum 2/3 Discharge
Static Heat loads on HTTS and LTTS must be performed individually due to shared flow meter
(A/B) shows redundancy to a sensor build into the 650 CM prototype &production

## Slide 12: Current cooldown flow path

## Slide 13: Max flow rate with existing system
Pressure at cavities < 2 bara
With existing cooldown valve, but adding 2” thick foam insulation to all the ¾” lines and 2” lines
With current cooldown valve (max Cv = 7.31)
Pressure near 6” recovery header is 6 psig (slightly below relief parallel plate set pressure)
Helium exiting cavities at 55 K (after picking up heat from the cavities)
Max flow rate is estimated to be ~40 g/s
Could replace the current bullet (max Cv = 7.31) with the max bullet available (max Cv = 12.76 based on WEKA catalog).
Max flow rate with larger bullet is estimated to be ~50 g/s based on the same assumptions from previous slide.

## Slide 14
650 CTL Flow Schematic
Existing PIP2IT transfer line
HB650MHz Cryomodule
Red: HTTS Supply. MV-614-H
Orange: LTTS Return- MV-616-H
Blue: 5K Supply- MV610-H
Green: LTTS Return- MV-612-H
Purple: HTTS Warm Helium injection
New CTL Transferline
HB650 Cryogenic Transferline (CTL) designed to repattern existing HWR bayonet locations to new HB650 bayonet locations
Design includes provision for HTTS warm mixing for controlled cooldown
Fabrication in progress (50% completed)

## Slide 15: 650 CTL model: Interface between 650 and PIP2-IT TL
HTTS Return to PIP2IT TL
HTTS Supply
From PIP2IT TL
LTTS Return
From 650
HTTS Supply
To 650
HTTS Return
From 650
LTTS Return
To PIP2IT TL
HTTS Warm Helium Injection

## Slide 16: 5K Supply W- tube for thermal bump
Bayonets to be installed on locations indicated by circles
Warm helium injection
W-tube currently installed at Meson Detector Building

## Slide 17: Relief Header Modifications Preliminary Design
2 bara Warm MAWP relief
GE Balanced Bellow Relief Valve : 400 g/s capacity.
2 bara Required capacity: 117 g/s
4 Bar Cold MAWP relief
Rupture disc: 4 bara
Fast Cooldown Bypass:
Weka DN80- Fast cooldown discharge to compressor suction.

## Slide 18
Existing HWR Relief header
Rupture Disk
Balanced Bellows Relief

## Slide 19: Flow Measurement
Install dual range thermal flow meter to the 6 inch suction header near coldbox​
  0-5 g/s​
  100 g/s​
To measure heat load on 5 K intercept and 40 K shield, flow can return to the cooldown line instead of returning to transfer line.

## Slide 20: CD Return Flow Transducer Location
Approximate Location of new Flow Transducer

## Slide 21: TRS ED0013632 (Draft) - Heat Load Measurement Requirements
 | LTTS flow rate | HTTS flow rate
unit | g/s | g/s
LB650 | 0.57 | 0.81
HB650 | 0.86 | 1.28
Reference
[1] ED0008200-revB
[2] ED0008555-rev1