## Slide 1: The ESRF Upgrade Programme Prototype Slab
D. Martin

## Slide 2: The ESRF Upgrade Programme Prototype Slab
The ESRF Upgrade program
Tolerances for the experimental hall slab
Slab design
Implementation
The EX2 Prototype slab measurements

## Slide 3: The ESRF Upgrade Program
The 286M€ Upgrade will focus
on five highlight areas:
  Nano-science and nanotechnology
  Pump-and-probe experiments and time-resolved science
  Science at extreme conditions
  Structural and functional biology and soft matter
  X-ray imaging
X-rays are an ideal tool to study nano-objects, as X-ray wavelengths are perfectly matched to this length scale.

## Slide 4: The ESRF Upgrade Program
ID16
EX2

## Slide 5: Long Synchrotron Radiation Beamlines
Long beamlines can be compared to a microscope. The principal measure of merit is spatial resolution.

## Slide 6: Long Beamlines
The size of the focused x-ray probe spot depends on:
  the source size,
  the distance between the source and the focusing optics p, and
  the working distance between optics and the experimental sample q.
  At the ESRF p=150 m and q=0.05 m so q/p=3000-1 → theoretical probe size ~10 nm

## Slide 7: Translation Tolerance
Tolerance is 10% of 50 nm probe size e = 5 nm over a period of 30 minutes
150 m
0.05 m
= 15 µm
U(trans) =
× 5nm

## Slide 8: Rotation Tolerance
Tolerance is 10% of 50 nm probe size e = 5 nm
over a period of 30 minutes
5 nm
0.05 m
= 100 nrad
U(rot) =

## Slide 9: Summary of the Static Slab Tolerances
Load Case | Deflection
Two pedestrians at 3 m | < 0.5 µm
Forklift at 10 m and in corridor | < 2.0 µm and < 200 nrad
Temperature over 12 hrs | < 2.0 µm and < 200 nrad
Temperature 20 °C outdoor change | < 1.0 µm and < 100 nrad
Slab tolerances are divided into static and dynamic load cases. The Survey and Alignment group can measure the statics load cases.

## Slide 10: Slab Tolerances to Building Tolerances
Tolerances must be converted into building tolerances
A key characteristic of concrete is its drying shrinkage
The design team stipulates that if shrinkage is below 300 µm per m then there is a good chance the ESRF tolerances can be respected

## Slide 11: Recent Light Source Slab Designs ESRF Design
Diamond UK
600 mm Steel reinforced concrete slab
600 mm diameter pile driven to the chalk layer
50 mm space
b
c
a
Soleil France
800 mm Steel reinforced concrete slab
600 mm diameter pile driven to the Fontainbleu sands
50 mm space
b
a
c
ALBA Spain
1000 mm Steel reinforced concrete slab
1700 mm compacted stone
b
a
Petra III Germany
500 mm fiber reinforced concrete slab
500 mm steel reinforced concrete slab
Bitumen layer
2000 mm compacted old concrete
a
d
c
b
Esrf France
350 mm steel reinforced concrete slab
2 mm Bitumen layer
100 mm finished concrete layer
550 mm rollcrete layer
Compacted earth
d
a
e
b
c

## Slide 12: Recent Light Source Slab Designs ESRF Design
Diamond UK
600 mm Steel reinforced concrete slab
600 mm diameter pile driven to the chalk layer
50 mm space
b
c
a
Soleil France
800 mm Steel reinforced concrete slab
600 mm diameter pile driven to the Fontainbleu sands
50 mm space
b
a
c
Technical Solutions:
  Piles to cross the poor soil to reach a good one (Soleil and Diamond)
  Compacted layers with new materials (Petra and Alba)
  Rollcrete layer plus natural soil (Esrf)
ALBA Spain
1000 mm Steel reinforced concrete slab
1700 mm compacted stone
b
a
Petra III Germany
500 mm fiber reinforced concrete slab
500 mm steel reinforced concrete slab
Bitumen layer
2000 mm compacted old concrete
a
d
c
b
Esrf France
300 mm steel reinforced concrete slab
2 mm Bitumen layer
100 mm finished concrete layer
550 mm rollcrete layer
Compacted earth
d
a
e
b
c

## Slide 13: Recent Light Source Slab Designs ESRF Design
According the features of the support the design of the high quality part includes:
  Steel reinforced concrete, with different thicknesses and steel ratio
  An additional layer with fiber reinforced concrete for Petra
  Bitumen layer for Petra and the Esrf to allow slippage without constraints during the drying period of the upper concrete layer(s)
Petra III Germany
500 mm fiber reinforced concrete slab
500 mm steel reinforced concrete slab
Bitumen layer
2000 mm compacted old concrete
a
d
c
b
Esrf France
350 mm steel reinforced concrete slab
2 mm Bitumen layer
100 mm finished concrete layer
550 mm rollcrete layer
Compacted earth
d
a
e
b
c

## Slide 14: EX2 Slab Soil Preparation
Cross section of the soil
the base soil is reached
Final survey to check the soil features (vertical deformation under pressure)
The soil has been prepared and well compacted

## Slide 15: Rollcrete Layer
Deliveries (250 trucks) and preparation
Compacting phases (8 times/layer)

## Slide 16: Rollcrete Layer
First layer and detail of edges
Final control with a gamma source

## Slide 17: EX2 Prototype Slab
Finishing concrete layer over the rollcrete layer
Bitumen layer

## Slide 18: EX2 Prototype Slab
Steelwork
Strain gauges and thermocouples

## Slide 19: EX2 Prototype Slab
Steel and pouring
Finishing

## Slide 20: EX2 Prototype Slab
Finished slab

## Slide 21: Prototype Slab Measuring Slab Shrinkage and Curling
AT401 Laser Tracker Measurements
HLS
Measurements

## Slide 22: Slab Shrinkage
Asymptote less than 180 µm per m

## Slide 23: Slab Shrinkage Strain Gauges
E1
E3
E2
E4,E6
E5
E5
E4
E6
E2
E3
E1
Plan
View
Side
View
Position of Strain Gauges

## Slide 24: Slab Shrinkage Strain Gauges

## Slide 25: Slab Shrinkage Bitumen Layer

## Slide 26: Overall Slab Curling

## Slide 27: Slab Movements due to Temperature Variation
T=constant
Over one day the sub-surface temperature doesn’t vary significantly
T=
Over the day air temperature varies

## Slide 28: Slab Movements due to Temperature Variation

## Slide 29: Slab Temperature Gradient Variations 23 to 29 March 2012

## Slide 30: Slab Movements due to Temperature Variation
Curling up to 20 µm per °C

## Slide 31: Slab Movements due to Temperature Variation
Bending up to 20 µrad per °C

## Slide 32: With special thanks to the other Survey and Alignment group members …
Bruno Perret, Laurent Maleval, Noel Levet
Christophe Lefevre, Daniel Schirr-Bonnans
Also to
Emmanuel Bruas Paul Mackrill and Chantal Argoud for the photographs