## Slide 1: Managing System Readiness
Ken Baggett
Department Head
Electrical Engineering Systems

## Slide 2: Outline
  Hot Checkout / System Readiness
  Process overview
  Process Execution
  Evolution
  Summary

## Slide 3: Regions
North East Spreader

## Slide 4: Motivation
On 10/14/12 two Septa magnets (YR) in the Northeast Spreader region caught on fire and sustained heavy damage.
Two direct causes:
  LCW valves for the dipoles were closed.
  A jumper in the box supply prevented the thermal switches from tripping the box supply on an over temperature fault.
Root causes were determined to be:
  Lack of adequate Work Control practices
  No systematic method of checking system readiness
Indirect Cause:
  Poor communication between System Owners and Operability

## Slide 5: YR Incident - Damaged Coils

## Slide 6: YR Fire - What went wrong? (cont.)
Contributing Causes:
  Poor communication between System Owners and Operability
    Very light attendance at RECO meetings by System Owners.
    Tools for System Owners/RECO inefficient or inadequate for information management.
Important to recognize the recommendation that tool requires two way input (system owners ↔ operations)

## Slide 7: Approach for Hot Checkout and System Readiness
Involve everyone
  Engage both technicians and management.
  Involve them in the system design
Be specific
  HCO software captures checkout of each component.
  Ensure work plans are developed for component HCO
Be efficient
  HCO software is web-based
  Include documentation/links in the tool.
  Displays multiple, dynamic reports.
Change the culture
  Ensure management transparently supports the program
  In our case, Accelerator Readiness Reviews (ARR) helped.

## Slide 8: Checklists
Checklists are used (and required) for each group performing work that could cause damage to personnel or the machine during beam operations.
HCO Checklists are:
  Maintained by work groups.
  Stored in the HCO database
  Documented using a configuration management process in software.

## Slide 9: Users
Technicians – Work to checkout components based on HCO requirements.
Group Leaders & Experts – System Experts, Group Leaders, Engineering Liaison work together to determine system readiness.
Management – Program Deputy (PD), Engineering Deputy, and Operability managers monitor/drive HCO progress based on beam destinations.
Operations – Verifies component status based on beam destinations prior to establishing beam for the PD’s accelerator program.

## Slide 10: Sign-off Process
New process utilizes a three-stage sign-off process
  Components are initially “Not Ready”.
  Technicians upgrade them to “Checked” once work is completed
  Group leaders upgrade them to “Ready” once work is reviewed.
Staff can add comments without having to change status.
Anyone can downgrade a component to “Not Ready”.
Once all groups have signed off on a component, the component name will be turned GREEN on the interface.

## Slide 11: Group Signoff
Group leader or technician can verify that all components in the region have been Checked/Ready.
The software interface:
  Is web-browser accessible.
  Shows all associated groups in work order.
  Provides for simple bulk signoff of components.
  Facilitates making, tracking, and reviewing comments.

## Slide 12: Readiness Status
Accelerator status:
  Can be filtered and displayed based on beam destination
  Incomplete HCO components
    RED
  Completed HCO components
    GREEN
  Checked HCO components
    YELLOW

## Slide 13: HCO Process Execution
HCO Program
  HCO team lead initially served as Program Deputy (PD)
    Now mature: no specific PD needed
Electrical Engineering Systems Deputy for Accelerator Reliability manages the process
Coordination and Sign-off
  Daily 0800 meetings to
    Refine the plan for the day.
    Communicate system status.
    Resolve any group and/or schedule conflicts.

## Slide 14: Overall Status

## Slide 15: Group-by-Group Progress

## Slide 16: Group-by-Group Status Breakdown

## Slide 17: Drill Down

## Slide 18: Updates / Additions

## Slide 19: Recent Activity Notices

## Slide 20: Masking Components

## Slide 21: Auto-generating Beamline Diagrams

## Slide 22: Problem Reporting

## Slide 23: Limitations
“Ops Centric” – Beam destination vs PSS segmentation
  Beam Authorization tool built to fill this gap
Auto downgrades don’t capture specialized work
  Workers focus on work vs downgrades
    Requires dedicated oversight
Readiness change / cascade notifications can get lost when too many emails
Adding new components or changing to unpowered can cause confusion
  Done when physicists require a change
Halls work autonomously
  Resolution of checkout differs hall->accelerator and hall->hall
A HCO team is necessary to manage the restoration process

## Slide 24: Has it worked?
Significant schedule and readiness issues associated with first run after long down.

## Slide 25: Summary
The System Readiness tool allows us to complete our HCO safely and efficiently
It also allows us to monitor component and system readiness during operations.
System ties together people, process, resources, and environment.
  Process focuses on system owners involvement.
  System requires groups to have a written checklist for components that may not have a safe failure mode.
  Technicians “Check” components.
  Group leaders responsible for saying components are “Ready”
  Operations can use tool to communicate readiness of components across shifts during runtime.