## Slide 1: Credited Controls and Instrumentation SNS Beam Power Limit System
Patrick Bong
Senior Protection Systems Engineer
Spallation Neutron Source at ORNL

## Slide 2: Beam Power Limit System
Credited control using FPGA
Instrumentation based on current transformers
Safety PLC calculates average beam power
Multiple shutoff paths through PPS and MPS
Standards guided engineering
Firmware verification
Requirements tracking using ReqTracer

## Slide 3: Using instrumentation to limit beam power to 2MW
Superconducting LINAC
RTBT
HEBT
Injection
Extraction
RF
~1300 MeV
Warm Linac
STS
2MW
0.7MW
Second Target Station
Linac PPS Segment:
New Cryomodules
Beam Power Limit System:
Upgrade to Safety PLC
FPGA added to credited controls
RTBT:
Add BPLS – interlock on max beam power
First Target Station

## Slide 4: BPLS Calculates Power Based on Beam Energy and Current
Superconducting LINAC
RTBT
HEBT
Injection
Extraction
RF
~1300 MeV
Warm Linac
Measure Energy
Measure Charge
STS
2MW
0.7MW
Second Target Station
Beam Energy calculated from critical device dipole DH13 current
Beam Current measured with Fast Current Transformer
Trips PPS if Beam Power > 2.145 MW for 60 seconds
Trips MPS if beam Power > 2 MW
First Target Station

## Slide 5: BPLS Design
DPU
DPU
PSI
PSI
Timing
Cycle Start
CPU
EPICS
CPU
Cycle Start
MPS
MPS
(Ethernet)
(PCIe)
Timing
Timing
Credited Engineering Control (CEC) Boundary
ADC
ADC
PPS
Mailbox
PLC
DIO
ADC
ADC
DIO
AFE
AFE
PLC
6
/
Mode: Init, Op, Cal, Maint, Fault
FST FCT Channel B
FTS FCT Channel A
Dipole DH13
DCCTs
MicroTCA
(Ethernet)
MicroTCA
(PCIe)
PSI Test
PSI Test
Pulse Trig
Pulse Trig
(Ethernet)

## Slide 6: BPLS Functional View
Safety Critical Functions

## Slide 7: Calculating Beam Power
FCT
  Fast Current Transformer
  Measures beam current pulse-to-pulse
  Calculated by DPU (FPGA)
DCCT
  Direct Current, Current Transformer
  Measures beam Energy
  Calculated by PLC
Calculation
  Eb = energy
  I(t) = current
  Tpulse = pulse length of the current
DPU
PPS
Mailbox
PLC
ADC
DIO
AFE
PLC
6
/
Mode: Init, Op, Cal, Maint, Fault
FTS FCT Channel A
Dipole DH13
DCCT

## Slide 8: DPU Interfaces
Charge Threshold,
Config, Status, Diag
Watchdog Reset
Test Pulse Req
Watchdog Req
Minor Fault
Major Fault
Fault Reset
Calibration Coil
Main Coil
Test Voltage Req
Test Pulse Trig
Cycle Start
Test Pulse Trig
FPGA
RS485
ADC
AFE
I/O
I/O
PLC
PSI
Test Pulse Ok
I/O
DPU Blocks
Main Safety Function
System Health
System Test
PSI
Cycle Start: locks internal machine cycle timer
Test Pulse Trig: Capturing Test Pulse data
AFE
Main Coil: Low Gain FCT for Beam Charge measurement
Calibration Coil: Test Pulse for system verification to test cable, AFE, and DPU
PLC
RS485 Read/Write: Beam Charge data
RS485 Read Only: Status & diagnostics
Reset & Faults: Major Fault indicates over Beam Charge Threshold & Minor Fault indicates a system error/failure
Watchdog: Interface verification
Test Pulse: Request and ok handshake
PLC/AFE: Test Voltage for Major Fault/ADC check

## Slide 9: DPU Firmware Block Diagram
UART RX
PLC Fault Reset
Modbus Interface
PLC RS485
UART TX
Modbus CRC
Machine Cycle Timing
Sliding Pulse Charge
Pulse Charge Integrator
ADC
ADC/Clock Initialization
ADC/Clock SPI
ADC Interface
Test Pulse
Test Pulse Gen Window
Test Pulse Meas Window
PLC I/O Interface
Baseline Integrator
Pulse Charge
Peak Pulse Charge A
Peak Pulse Charge B
Modbus Registers
Test Pulse Generate
Beam Charge Integrator
Beam Charge Comparator
Major Fault
PLC Major Fault
PLC Minor Fault
PLC Watchdog Req
PLC Watchdog Reset
PLC Test Pulse Ok
AFE Cal Coil
AFE Main Coil
PLC
RS485
Test Gen
Fault
Test Meas
Fault
PSI Cycle Start
Beam Charge
AFE/PSI Test Pulse Trigger
PLC Test Pulse Req
Single Event Upset

## Slide 10: Calculating Charge Without Cycle Start
Internal Timer 2
Use 2, 16.67 msec windows offset by 5 µsec
When one 16.67 msec window lands on a pulse, the other is still valid
Taking the larger value results in a valid measurement
Internal Timer 2
Internal Timer 2
Max
Max
Max
Internal Timer 1
Internal Timer 1
Internal Timer 1
Max
Max
Max
Baseline
Baseline
Baseline
Baseline
Baseline
Baseline

## Slide 11: DO-254, Design Assurance Guidance for Airborne Electronic Hardware Standard
DO-254 is a requirements-driven process-oriented safety standard used for commercial electronics that go into aircraft
Applies to the quality assurance of custom micro-coded components such as field programmable gate arrays (FPGA), programmable logic devices (PLD), and application-specific integrated circuits (ASIC)
A walkthrough of the standard applied the design assurance levels to the SNS FSAD-PF to develop a risk matrix
The FPGA parts of the BPLS are engineered using applicable parts of the standard and is used as a best engineering practice

## Slide 12: DO-254 Design Assurance Levels (DALs)
The SNS FSAD definitions of consequence are similar to the DO-254 descriptions
The FSAD consequences were mapped to the DO-254 matrix to determine Design Assurance Levels
DO-254 DAL C (Major) was determined to be the appropriate classification for the BPLS
The acceptable level of risk is equivalent to SIL 2
The analysis is documented in a cross walk (PPUP-406-TD0001-R00)

## Slide 13: IEC 61511 and ANSI/ISA S84.01
Functional Safety of Electrical/Electronic/Programmable Electronic Safety-Related Systems for the Process Industries Sector
Captures best practice for complex systems
Performance based requirements
Used as guidance for the development of PLC based PPS systems

## Slide 14: Safety reliability requires diagnostics and self-test
IEC 615111/61508 Safety reliability is reached by:
Robust design
Redundancy
Verification and Validation (V&V)
  Includes modeling and simulation – extensive capability in digital
Diagnostics and Self-test
  Digital affords greater coverage AND efficient use of resources
 | Hardware Fault Tolerance (Redundancy) N+1 required for safe operation |  | 
Detectable Faults | 0 | 1 | 3
< 60% | Not Allowed | SIL 1 | SIL 2
60% - < 90% | SIL 1 | SIL 2 | SIL 3
90% - < 99% | SIL 2 | SIL 3 | SIL 4
>= 99% | SIL 3 | SIL 4 | SIL 4
Table 3
IEC 61508-2 “Functional safety of electrical/electronic/programmable electronic safety related systems”
Target for BPLS
1. SNS uses IEC 61511, formerly ISA S84, in the design of safety systems

## Slide 15: Federal and DOE Requirements
10 CFR 835, Occupational Radiation Protection
  This section of the Code of Federal Regulations contains requirements for radiation protection that the laboratory must meet to comply with Federal law
DOE O 420.2C, Safety of Accelerator Facilities
  This directive establishes accelerator specific safety requirements to promote the safe operation and ensure the protection of workers
DOE G 420.2-1A Accelerator Facility Safety Implementation Guide
  This guide provides supplemental information to help accelerator facilities implement the requirements of the order
DOE O 414.1D, Quality Assurance
  This order establishes the requirement for a Quality Assurance Program (QAP) and defines the necessary steps to implement the program

## Slide 16: IEC 62443 Standard
IEC 62443, Cyber Security for Industrial Automation and Control Systems
  Provides guidelines for establishing a cyber security program for industrial automation and control systems
  In practice, the safety system network is connected to the controls network through a firewall
  Programming laptops are not allowed to be connected to the internet
The safety system is engineered using parts of the standard and is used as a best engineering practice

## Slide 17: Firmware Verification Methodology & Tools
Each firmware module is individually tested (‘linted’) using BluePearl RTL analysis
  Standard syntax checking
  Common mistakes not caught by simulation
    Constant false / true statements
    Missing process sensitivity signals
    Range mismatch
    Ambiguous coding styles
  Limited timing analysis
  Enforces IEC62566 section 8 (except 8.3.4(f))

## Slide 18: Firmware Simulation Methodology & Tools
Each firmware module is individually simulated using Xilinx Vivado simultion using Xilinx XSI interface & Python 3
  Multiple unit tests per module (typically at least 2)
  Easily extended to corner cases as needed
  Some modules are fully coverage-tested for all inputs & outputs
  Others are too complex - impossible to validate fully without making assumptions about the code under test - use ‘Monte Carlo’ method
Overall firmware is simulated using a combination of simulated & measured input data

## Slide 19: ReqTracer Tool to Manage Requirements
ReqTracer is a requirements traceability solution
Links development & verification documents with formal requirements.
Ability to trace and manage design requirements from specification to implementation and verification.

## Slide 20: ReqTracer tool will ensure requirements are covered & tested in the BPLS project
ReqTracer is a requirements traceability solution. It links development & verification documents to formal requirements.
ReqTracer has ability to trace and manage design requirements from specification through implementation and verification.
Key Features:
Connect requirements from many source files, databases
Supports standards like DO-254, ISO 26262, IEC 61508 and IEC 60601
Links relationships and dependencies
Immediate notification of requirement changes, additions and deletions
Confirms that all design requirements have been implemented and fully tested

## Slide 21: Summary
The BPLS is the first credited control at SNS to use a firmware programmed device for safety
A standard used for airborne safety will be used as guidance
The DO-254 standard has close alignment with the IEC standard and Safety Integrity Levels
ReqTracer has been instrumental with connecting component requirements to the System Requirements Document (SRD)