## Slide 1: Construction Status of Personnel Protection System for FRIB
Masanori Ikegami Facility of Rare Isotope Beams, Michigan State University

## Slide 2: Outline
Background
  Facility layout
  Major design parameters
  Phased Accelerator Readiness Reviews (ARR’s)
Personnel Protection System (PPS) for Linac
  Radiation Safety System (RSS)
  Oxygen Deficiency Hazard Control System (ODHCS)
Extension of PPS to experimental area
Summary

## Slide 3: Layout and Major Parameters for FRIB
Delivers primary beams to production target to support physics experiment utilizing various secondary particles
Accelerate ion species up to 238U with energies of higer than 200 MeV/u
Provide beam power up to 400 kW
Continuous Wave (CW) operation
Constructed beside the existing NSCL (National Superconducting Cyclotron Laboratory) building
Utilize experimental beam lines for NSCL

## Slide 4: FRIB Technical Construction 2014 – 2021
Superconducting Radio Frequency (SRF) technology extensively adopted
  324 SRF cavities in 46 cryomodules in total to accelerate heavy ion beams from 0.5 MeV/u to ≥ 200 MeV/u
Folded layout with 3 Linac Segments (LSs) connected with 2 Folding Segments (FSs)
FRIB driver linac in accelerator tunnel

## Slide 5: Phased Commissioning and Accelerator Readiness Reviews
LS1
LS3
BDS
FS2
1
2
3
5
LS2
FS1
4
6
Commissioning of FRIB accelerator is conducted in phases
Phase | Area with beam | ARR | 
ARR01 | Ion source, Low Energy Beam Transport (LEBT), Radio Frequency Quadrupole (RFQ), Medium Energy Beam Transport (MEBT) | 07/2017 | ✔
ARR02 | Linac Segment (LS) 1 (β=0.041 cryomodules) | 05/2018 | ✔
ARR03 | Rest of LS1 and first dipole of Folding Segment (FS) 1 | 02/2019 | ✔
ARR04 | Rest of FS1, LS2, and part of FS2 to straight dump | 03/2020 | ✔
ARR05 | FS2, LS3, part of Beam Delivery System (BDS) to straight dump | 04/2021 | ✔
ARR06 | BDS, target hall pre-separator | 10/2021 | 
ARR07 | Fragment separator, FRIB project completion | 01/2022 | 

## Slide 6: Hazards Introduced in Phase
Beam parameter for commissioning are limited to introduced hazard in phase
Phase | Max. Beam Energy | Max. Primary Beam Power/Current | Max. Secondary Beam Power | Ion Species | Newly Introduced Hazards | 
ARR01 | 1 MeV/u | N/A | N/A | All stable ions except hydrogen | X ray from ion source | ✔
ARR02 | 2.4 MeV/u | 100 euA | N/A | 40Ar, 48Ca, 58Ni, 64Ni, 78Kr, 86Kr, 82Se, 92Mo, 124Xe, and 238U | Oxygen Deficiency Hazard, X-ray from Superconducting RF cavities | ✔
ARR03 | 27.5 MeV/u | 500 W | N/A | O to Xe | Neutron from beam-material interaction, long-lived isotope from beam-material interaction | ✔
ARR04 | 257 MeV/u | 135 W | N/A | O to Bi (extended up to U later) | No new hazards, higher energy but lower power than ARR03, area of hazard extended | ✔
ARR05 | 257 MeV/u | 135 W | N/A | 86Kr, 129Xe | No new hazards, area of hazard extended | ✔
ARR06 | 257 MeV/u | 135 W | 1 W | 86Kr | No new hazards, area of hazard extended | 
ARR07 | 257 MeV/u | 135 W | 1 W | 86Kr | No new hazards, area of hazard extended | 

## Slide 7: Personnel Protection System Being Implemented in Phase with Commissioning
Personnel Protection System (PPS) is designed to address
  Radiological hazards for workers and the public from prompt exposure where significant exposure is possible without action
  Oxygen Deficiency Hazard (ODH) conditions from a major release of cryogen
PPS for FRIB has been implemented in phase to mitigate hazards warranted for the phase of commissioning
Radiation Safety System (RSS)
Oxygen Deficiency Hazard Control System (ODHCS)
Radiation Control System (RCS)
Access Control System (ACS)
Personnel Protection System (PPS)

## Slide 8: Access Control System for Linac Radiation Safety System (RSS) in Operation
Linac Access Control System (ACS) supports sweep of linac tunnel
  Sweep buttons
  Gate/door switches
  Lights and sounders
  Tunnel access state indicators
Linac ACS shuts off beam with beam inhibit devices (on the next slide) at detection of activation of e-stop buttons or opening of doors with tunnel secured state
Sweep path for linac tunnel
Door switches
E-stop button
Entrance signs
PPS rack

## Slide 9: Beam Inhibit Devices for Linac RSS
Beam plug
AC contactor for Artemis high voltage (defense in depth)
AC and DC contactors for electrostatic bends high voltage
3 Beam Inhibit Devices (BIDs)
  Beam plug in Low Energy Beam Transport (LEBT)
  AC and DC contactors for electrostatic bends high voltage
  Beam inhibit with AC contactor for Artemis ion source high voltage as defense in depth
9 AC contactors for RF amplifiers for SRF cavities in cryomodules
AC contactor

## Slide 10: Radiation Monitors for Linac RSS in Operation
HVAC OUT shaft (ground level)
West loading hatch (ground level)
East loading hatch
(ground level)
Cryogenic distribution shaft (ground level)
Inside target hall (basement level)
Neutron monitor
HVAC IN shaft (ground level)
Front-end drop (ground level)
Conduits near FS2 dump (ground level)
Decontamination room (basement level)
Interlocked neutron monitors in accessible area to shut off beam at detection of ≥ 2 mrem/h
Neutron monitor installed at front-end drop

## Slide 11: Oxygen Deficiency Hazard Controls Systems in Operation
Cryoplant Oxygen Deficiency Hazard Control System (ODHCS) in operation since August 2017
  6 Oxygen Deficiency Hazard (ODH) monitors with 24 air sampling points covering cold box room, warm compressor room, and cryo control room
Linac tunnel ODHCS in operation since March 2018
  3 ODH monitors with 12 air sampling points
PPS rack
Horn
ODH monitor
Warning light

## Slide 12: Network for Personnel Protection System Isolated from General Controls
General Controls
Personnel Protection System (PPS)
Remote IO
Safety PLC
Boundary with no
network connection
Contact
signal
DO
PLC
DI
Data Archiver
Work Station
Controls
network
Input / Output Controller
PLC
DO
Hardwires
Hardwires
Radiation monitor/ODH monitor
Serial-Ether Converter

## Slide 13: ARR05 Beam Commissioning Conducted with COVID-19 Safeguards
ARR05 beam commissioning conducted from main control room and 3 satellite control rooms to have social distance
Main control room and satellite control rooms are connected with a Zoom session
Main control room
One of satellite control rooms (AP control room)

## Slide 14: Radiation Safety System Being Extended to Experimental Area
FRIB will have 3 Programmable Logic Controller (PLC)-based Radiation Safety Systems (RSS) each of which has its own safety PLC
  Linac RSS
  Target Facility RSS
  Experimental vault RSS
Interface of Experimental Vaults RSS will be changed when integrated with FRIB
Target Facility RSS (In construction)
Experimental Vaults RSS
(Formerly NSCL RSS)
Linac RSS (In operation)

## Slide 15: Five Access Control Areas for Target Facility RSS being Implemented
Ground Level
Basement Level
Sub-basement Level
Non-Conventional Utility (NCU) rooms
Filter room
Vertical pre-separator room and transfer hall
Target hall
Five access control areas are administered by Target Facility RSS (PLC based)
Being implemented with the same standard with Linac RSS to benefit from its operational experience
Waste handling room

## Slide 16: Fast Beam Containment System Being Developed for Future High Power Operation
Fast Beam Containment System (FBCS) being developed to shut off beam within ~ 1 ms at detection of elevated radiation dose rate to protect against unintentional delivery of high power beam to secondary beam line
Prototype being installed for testing in ARR06 beam commissioning (not as a safety system yet)
Ion Chamber
Fiber transport to RF switch (~700 ft.)
RF Switch
Comparator
Signal transport to comparator
Sub-system | Function | Status
Ion chamber | Detect elevated radiation | Delivered and Acceptance Criteria Listing (ACL) test complete
Comparator | Implement trip threshold | Prototyped and tested with RF switch
Fiber transport | Transport trip signal to RF switch | Prototype test conducted with 100 ft.
RF Switch | Inhibit beam by shutting of RF for RFQ | Prototyped and tested with comparator
Safety PLC | Provide health monitoring and machine mode control | Interface being finalized
Ion chambers for FBCS

## Slide 17: Planned Radiation Monitor Layout
Neutron monitor layout in Room 1500 and experimental vaults is the same with NSCL
  Surrounding secured vault
Plan to add ion chamber pairs near wall plugs to experimental vaults
Interlocked neutron monitor
U: upper level
B: basement level
Others: ground level
Interlocked ion chamber pair
U
U
U
U
B
U
B
B

## Slide 18: Interface between RSS’s
Linac RSS
Target Facility RSS
Exp. Vault RSS
A
B
C
D
 | Hardwires
A | Target ready for beam (including radiation not high) BDS BID status (Linac RSS has own sensors)
B | Beam permit to target issued
C | Vault ready for beam (including radiation not high) Beam plug status (Target and Transfer Line RSS has own sensors)
BDS BID
Beam stops and wall plugs
FE BIDs, SRF RF
Fast Beam Containment System
F
G
RFQ RF BID
 | Hardwires
D | Beam permit to beamline issued
E | Vault ready for beam (including radiation not high) Beam plug status (Target and Transfer Line RSS has own sensors)
F | Radiation high
G | Target ready for beam
E
T10501-CM-000117

## Slide 19: Construction Status and Path Forward
Target Facility RSS for ARR06 constructed and being validated
ARR06 review in late October 2021
Target Facility RSS for ARR07 being constructed to be integrated with Experimental Vault RSS in December 2021
ARR07 review in January 2022
Commencement of user operation in early 2022

## Slide 20: Summary
FRIB is being commissioned in phase with construction
Hazards are introduced in phase and PPS has been implemented to mitigate the hazards warranted for each phase
PPS for linac constructed and in operation
PPS for experimental area is being established to support final phases of commissioning
PPS construction is on track to support early completion of FRIB project in January 2022 and commencement of user operation in early 2022

## Slide 21: Backup

## Slide 22: Power Ramp Up to the Frontier of Heavy Ion Facilities
Riken is holding current record of highest heavy ion beam power
  Presently 14.5 kW of Zn-70 and 9.6 kW for uranium
  Aiming at ~ 90 kW with improvements like charge stripper ring
FRIB aims at ramping up to 400 kW primary beam power in 6 years after commencement of user operations