## Slide 1
Workshop on Maintaining PIP-II within the Accelerator Complex
Matthew Howell
Cryogenics Group Leader
July 15, 2021
Cryo Plant and Linac Operations at SNS

## Slide 2: Outline
Central Helium Liquefier (CHL) overview
CHL availability
CHL maintenance
Superconducting Linac (SCL) Overview
SCL availability
SCL maintenance
Summary

## Slide 3
CHL Block Flow Diagram
1st Stage Compressor
2nd Stage Compressor
To LDS Shield Supply
He Dewar
To LDS
Primary
Supply
From LDS
Shield Supply
From LDS
Primary
Supply
To LDS
Shield Return
2K Cold Box
4K Cold Box

## Slide 4: SNS CHL

## Slide 5: CHL Availability Statistics
The availability of the CHL is outstanding
Fiscal Year
Availability %
Availability %
Down time hrs

## Slide 6: Available time for Maintenance
Maintenance outages
  Two outages per year lasting 4 – 9 weeks
Scheduled maintenance days
  Every other Tuesday
Coordinate the cryogenic plant and the superconducting linac maintenance during these outages to avoid beam interruptions

## Slide 7: CHL Maintenance
Maintenance strategy
  Keep the system cold to avoid thermal cycling
  Avoid any outage of the CHL more than eight hours
  Purify all helium entering the system
Compressors
  One spare in line compressor for both first and second stage
    All compressors ready to operate during a run
  Coordinate annual maintenance during scheduled maintenance outages
  Smaller maintenance requirements conducted during maintenance days
  Routine rotation of compressors occurs every Friday
Other maintenance scheduled and coordinated for maintenance outages
  Controls
  Ancillary systems
  Cold box issues
Compressor 4 being craned into place

## Slide 8: SCL Overview
23 operating cryomodules
  Containing 81 Superconducting cavities
  Operating temperature of 2.1 K
  Contains a 35K thermal shield
  Nine empty slots to allow expansion
  Tunnel equipped with ancillary systems
    Beam line and insulating vacuum pumping
    Water cooling for couplers and magnets
    3 atmosphere helium, guard vacuum and cooldown headers to support cryomodule operation and maintenance
Segmented design
  Cryomodules are separated from the adjacent cryomodules by warm sections containing beam pipes and quadrupoles
  Cryomodules are connected to the cryogenic plant through 4 u-tubes
Cryomodules in SNS Linac
Cryomodule 15 in Linac
U-tube
Warm Section

## Slide 9: SCL Repairs
Determine whether repair can be made in the tunnel or if the cryomodule must be removed
  External to the tunnel repairs
    Spare cryomodules available to support external repairs
    Helium leaks on feed throughs
    HOM Feed through replacement
  Internal to the tunnel repairs
    Tuner repairs
    Instrumentation
    Thermal cycling to regain gradient
    Apply plasma processing to increase gradient
  Repairs previously done external to the tunnel can be done internal to the tunnel as a result of development
    Coupler replacement

## Slide 10: SCL Availability Statistics
The availability of the SCL is outstanding
Chart: 
| FY11 | FY12 | FY13 | FY14 | FY15 | FY16 | FY17 | FY18 | FY19 | FY20 | FY21
SRF cavities/Cryomodule | 99.656 | 99.6352 | 99.788 | 99.6575 | 99.6205 | 99.767 | 99.4689 | 99.53 | 99.6 | 99.3 | 99.2
SCL including whole supporting systems | 97.9822 | 98.1739 | 97.6113 | 97.9676 | 98.4788 | 97.3557 | 97.994 | 97.96 | 98.6 | 98.3 | 98.3
FY21 is as of end of May

## Slide 11: Fabricated High and Medium Beta Spare Cryomodules
Spares
  Allows for removal of cryomodules for repair while maintaining the same beam energy
  HB spare cryomodule completed and installed in summer of 2012
  MB spare cryomodule completed and installed in winter of 2020
  Based on our experience, a spare PPU cryomodule has been added to the scope of the project
HB CM Spare Assembly Effort
MB Spare

## Slide 12: Repairs requiring cryomodule removed from tunnel
HOM – Higher Order Mode
  Not necessary for SNS
  Only installed to protect against the unknown
  About half leaked between insulating vacuum and beam line vacuum
Helium Leaks
  Predominantly from diode feed throughs in the end cans
Blanking off HOM feed through port
HOM Feed through flange
Decontamination Tent for Cryomodule Repair

## Slide 13: Repairs completed in tunnel
Tuner repairs
  Harmonic drive wearing
  Replacement of tuner stepper motors
  Piezo tuners breaking due to mechanical stress
Instrumentation
  Replacement of pressure, temperature, and RF instruments
Plasma
  Developed though a comprehensive R&D plan to recover and improve cavity gradients
  Now able to deploy in the tunnel
CAD model of an SNS Tuner
Harmonic Drive Assembly
First Plasma Processing of a Cryomodule in the Tunnel

## Slide 14: Developing methodology to do more repair in tunnel
SNS has experienced 7 coupler window leaks
  Leaks were 10e-7 Torr L/s or lower
  Previously repaired external to the tunnel in the clean room as shown
    Repairs 4 with this methodology
  Methodology developed to build a temporary clean room around an installed cryomodule and replace the coupler
    Repaired 3 with this methodology
    One more schedule for the winter of 2021
Work on coupler in clean room
Coupler install in clean room
Local clean room setup for CM repair
Installation of coupler
in the tunnel

## Slide 15: Summary
The CHL and SCL have been very reliable components of the SNS accelerator complex
Maintenance strategies have been utilized to ensure the reliability and availability of the machine is maintained
Spare high and medium beta cryomodules are available to facilitate cryomodule repairs
Methodologies are evolving to conduct more repairs in the tunnel to reduce the amount of time to complete them