AD/Cryogenics Dept

Shutdown 2006 Status Report

5/5/2006 (Makara/Olesen)

# Cryo Operations:

- Tevatron at LN2 temperature and LN2 usage is stable with vendor deliveries running only 2-3 truckloads per day due to the Tevatron being 1/6 at room temperature.  Helium losses are slightly down at 12 kscf/day (1/3 of normal during Tev operations); some helium being replenished from A0 GHe Recovery of test caves.

- A1 and A3 are at room temperature and isolated with LOTO.

D1 and F4 are also at room temperature, have been reconnected by Cryo, and are under helium flow.  D1 cooldown permit signoff has been completed and cooldown to LN2 temperature will commence soon.

F4 cooldown will wait until TEL-1 is re-installed.

A3 has been completed by MSD, but spool piece conning towers retrofit by TD is in progress.

- Pbar D60 Debuncher tanks were cooled down to LHe temperature after Division sign-off.

- ACNET application programs relating to FRIG operations continue to be tested on Linux consoles.

- Nitrogen Reliquefier plant was started and cooled down successfully.  It was shut off later for some minor repairs and due to lack of sufficient nitrogen gas coming from Tevatron due to E0 still being on generator power. We plan to cool it down again next week.

- CHL Helium Compr “C” was started for testing and purification but was shut down due to 2nd stage suction cylinder valve failure.

- MCR monitoring cryo operations.

CHL Maintenance:

- General facility maintenance is in progress, including testing of relief valves per FESHM.

- Helium Compr “A” cooling tower installation has been completed and system testing has started. Motor switchgear mechanical binding needs to be addressed by FESS.

- Helium Compr “D” overhaul is almost completed but awaiting installation of cylinder valves.

- Helium Coldbox-2 controls upgrade is in progress.

- Mobile Helium Purifier is being derimed at room temperature and piping modified.

FRIG Maintenance:

- Various FRIG bldg vacuum maintenance and instrumentation repairs (e.g. lost charge on VPTs) are in progress, as well as support work on houses at room temperature and other equipment as things fail even during the shutdown period.

- Various Mycom compressor maintenance: leak hunting and general repairs.

- Wet expanders overhauls have been completed ringwide.

- Reciprocating cold compressors are being overhauled for A4, B1, and C4.

  	Kautzky relief valves have been replaced ringwide and retorquing clamps are in progress.  One KV at A3 was found with broken poppet tip that was blown into the helium suction header, though this KV still functioned properly.

- Helium to atm leaks on conning tower quick-disconnect fittings and safety lead flow glands are being found and fixed.

Meeting Notes: