## Slide 1
The JASMIN Collaboration
Radio-colloid formation in cooling-waters
in 120-GeV proton accelerator at fermilab
2/16/2012
Speaker: Hiroshi MATSUMURA
(KEK, JAPAN)
A. Investigation in cooling-water systems in fermilab
B. Investigation in Cu/H2O bombarded with 120-GeV protons at M01
---EXPERIMENTS---

## Slide 2
A. Investigation in cooling-water systems in fermilab
B. Investigation in Cu/H2O bombarded with 120-GeV protons at M01 (will be talked in later session)
EXPERIMENTS

## Slide 3: Radionuclides in cooling-waters
pipe (Al, SUS, Cu, etc.)
target (Al, Ni, Ta, etc.)
water (H2O)
Nuclear reaction
Radionuclide
Primary particle
Secondary particle
recoil
primary particle
1
dissolve
recoil
recoil
dissolve
primary particle
primary particle
secondary particle
secondary
particle
2
2
3
3
recoil
dissolve
primary particle
primary particle
4
4

## Slide 4: Removal of radionuclides from waters
radioactive
water
non-radioactive
water
IN
OUT
pure water
dirty water
(1) in order to keep water pure for accelerator materials
(2) in order to remove radionuclides for radioactivity control
Cooling-water system is equipped with a deionizer
ion-exchange resin
Deionizer
ion
water
resin
If deionizer can collect radionuclides completely, ...

## Slide 5: Colloid formation of radionuclides?!
FIG. Distribution of radionuclides in the demineralizer of K2K at KEK in Japan.
(H. Matsumura et al., Nuclear Technology, 168, 979 (2009).)
Y-88, Rh-101g, Rh-102m, and Be-7 showed weak retention to ion-exchange resin.
12 GeV
protons
1st magnetic horn
2nd magnetic horn
60 L/min
Al target
The K2K target and magnetic horns
in KEK, JAPAN
FIG.1 The water cooling system for the target and magnetic horns in the K2K experiment.
ion-exchange resin
(AmberLite, MB-2)
due to colloid formation?!
This incomplete adsorption
will cause serious problems.
Deionizer

## Slide 6: Serious problem at J-PARC
FIG. Variation of Be-7 activity in the cooling-water
for the T2K magnetic horns in function of duration of deionization.
Duration of deionization (hours)
Run36: 11/16-12/25/2010
Run37: 01/16-02/28/2011
Limit of Be-7 activity for drain is 30 Bq/ml
Although we have to remove Be-7 more efficiently (>99.9%),
~1% of Be-7 was remaining in the cooling-water in spite of long deionization.
T2K will be powered up in the near future.
NOTE
~1% of Be-7
was remaining
We have to understand behavior of radionuclides
in cooling-waters and do something.
Cooling-water system is drained and refilled at regular intervals.
5
Our forebodings proved true in the T2K magnetic horns at J-PARC

## Slide 7: Investigation on waters at fermilab
NuMI
Tevatron
Main Injector
PbarTS
M-test
D0
CDF
M01
Wilson Hall
HIL
120-GeV proton accelerator in fermilab (USA)
We performed investigation on colloid formation of radionuclides in the cooling-waters for 120-GeV proton accelerator at NuMI and Pbar TS in fermilab.
We did not wait for proving the forebodings of the J-PARC problem.
When we found the weak retention of radionuclides to ion-exchange resin at the K2K horns, we decided to investigate on radionuclides in the cooling-water soon.

## Slide 8: Sampling of cooling-waters
We collected 8 cooling-water samples from the NuMI and Pbar systems on
(1) Feb. 2010,
(2) Dec. 2010,
(3) Sep. 2011.
120-GeV p
6
7
8

## Slide 9: Data of the cooling-water systems
Important data on the cooling-water systems

## Slide 10
RESULTS

## Slide 11: Detected radionuclides in the waters
arranged in order of activity
I will focus to Be-7 in this talk.
The cooling waters contained various radionuclides depending on materials contacted with water.

## Slide 12: Activity of Be-7 in the waters
Activities were quite different among the cooling-water systems.
higher activity
increased
lower activity
1
2
Activity is independent of the sampling date.
High activity: the Pbar pulse magnet and dump
Low activity: the NuMI target, horns, decay pipe, and absorber, and Pbar lens
In only NuMI absorber, the activity increased.
no deionizer
with deionizer

## Slide 13: Remaining rate of Be-7 in water
Remaining rate of Be-7 =
ABe-7
AH-3
σH-3
σBe-7
SFH-3
SFBe-7
.
.
m
A: Activity
σ: Cross section
SF: Saturation factor
* Leaking and decomposition of water
during machine operation were ignored.
σH-3
σBe-7
= 6.1
where
Be-7
Be-7
Be-7
H-3
H-3
H-3
low remaining rate
no deionizer
(only string filter)
high remaining rate
10
with deionizer

## Slide 14: Colloid rates of Be-7
Very high colloid rates were measured in the systems with deionizer.
1
2
cent-
rifuge
cut off
ion
colloid
3 nm pore
ultrafiltration
membranes
Low colloid rates were measured in the systems without deionizer.
low
colloid rate
high
colloid rate
no deionizer
(1) Most of ions were removed by deionizer.
(2) Colloids were remaining in the cooling-water.
ultrafiltration unit
4000rpm
10min
with deionizer

## Slide 15: Charge of radio-colloid
Anion exchange column
Cation exchange column
(Dowex 1X8 100-200 mesh)
(Dowex 50WX8 100-200 mesh)
resin: 1 mL
Be-7 passing rate (%)
Be-7 passing rate (%)
resin: 1 mL
+
+
-
-
+
+
-
-
1
2
Most of Be-7 (~100%) was adsorbed in cation-exchange column.
Small fraction of Be-7 was passed through cation-exchange column.
(1) Most of Be-7 colloids have plus charge.
(2) Weak retention power of Be-7 colloid on cation-exchange resin was observed.
3
Most of Be-7 (~100%) was passed through anion-exchange column.
1
2
3
Water samples (100 mL)
were passed thorough
cation-exchange column and anion-exchange column.

## Slide 16: Summary (experiment A)
(1) cooling waters contained various radionuclides depending on materials contacted with water,
(2) activity and colloid rate of radionuclides in cooling-water depended on deionizer,
(3) remaining of Be-7 in the cooling-waters was due to weak retention of the Be-7 colloids to cation-exchange resin in deionizer.
In cooling-water for high-energy accelerators,
we found characteristics of radionuclides as following.
We obtained a law of radionuclide behavior in cooling-water. We are considering a new removal method of radio-colloid from cooling-water.
Colloid resolution during operation?
Colloid resolution after operation?

## Slide 17
A. Investigation in cooling-water systems in fermilab
B. Investigation in Cu/H2O bombarded with 120-GeV protons at M01 (will be talked in later session)
EXPERIMENTS

## Slide 18
Thank you very much
for your valuable supports
for our experiments.