## Slide 1: Cryosystem design
March 15th 2012
Torsten Koettig
Lawrence Berkeley National Laboratory

## Slide 2: Cryogenic issues
Separate Cryomodules
Operating temperature 1.8 K, generated separately inside CM’s
Heat load per CM =f(Q0, operating gradient, …)
Cryoplant size (1 vs. 2 units). Estimated load >4.5 kW @ 1.8 K
Heat load from HOM, power coupler etc.
Cooling capacity for SC undulators at 4.5 K => 200 W per beamline
Critical heat flux - Cavitation

## Slide 3: Cryosystem
Cryogenic efficiency assumptions
Temperature level in K | COP in Wel/Wcooling p. | Source | ~ Multiplier to 4.5 K equivalent
1.8 | 930 | CERN | 4
2.0 | 773 | FNAL | 3
4.5 | 230 – 245 | CERN | 1
5 - 8 | 190 | FNAL | 0.75
40 - 50 | 16.5 | KEK | 1/14
40 - 80 | 18.4 | FNAL | 1/13

## Slide 4: He II transport properties
Mini-channels
„Ekin, Experimental Techniques for lowTemeperature Measurements“
Large cross section
„van Sciver, Helium cryogenics“
m = 3 … 3.4

## Slide 5: Cryogenic circuit

## Slide 6
Feed pipe of a cavity
Cryogenics for CM’s

## Slide 7
CM heat exchanger
Plate heat exchanger m=4.5 g/s
.
ΔpVLP = 88 Pa
= 0.88 mbar

## Slide 8
1.8K 2.5K 4K 5K 6K
CM heat exchanger
Δh=19 J/g
=> 180 W => 9.5 g/s

## Slide 9
Feed pipe of a cavity
Cryogenics for CM’s

## Slide 10: Two phase pipe diameter
Input parameter: - vvapor= 5 m/s vapor space is upper half of the pipe
- TSVP= 1.8 K
- L2phase-p= 11 m
- Qcavity= 25.7 W/cavity, 7 cavities per CM, Q = 180 W
d2phase-p= 94 mm
.
.

## Slide 11
Feed pipe of a cavity
T1=1.8 K, ΔT=20 mK, L=0.25 m, Q=25 W
=> d=6 cm
.
Chart: Maximum heat flux
| 1.82 | 1.84 | 1.86 | 1.88 | 1.9 | 1.92 | 1.94 | 1.96 | 1.98 | 2.0 | 2.02 | 2.04 | 2.06 | 2.08 | 2.1 | 2.12 | 2.14 | 2.16
 | 0.72606 | 0.89955 | 1.0228 | 1.1219 | 1.2056 | 1.2778 | 1.3408 | 1.3954 | 1.4423 | 1.4819 | 1.5144 | 1.5399 | 1.5587 | 1.5715 | 1.5791 | 1.5826 | 1.5836 | 1.5837
OFHC Cu: d=75 cm
Feed pipe diameter

## Slide 12
Cryogenic distribution line
Cryogenic transfer line
Cryoplant at ~400 m
NGLS layout

## Slide 13
di=360 mm
Cryogenic transfer line - GHe return pipe

## Slide 14
di=360 mm
Cryogenic transfer line - GHe return pipe

## Slide 15
Cryogenic transfer line - GHe return pipe
di=360 mm

## Slide 16
Cryogenic transfer line - GHe return pipe

## Slide 17
Critical heat flux
He II level
Power supply
Heater
Cryostat
Heat and mass flow are
limited by a critical velocity:
v > vcr
Superfluid behavior becomes
non-linear
k and η
Formation of gas bubbles at
the surface of the heater
In He II recondensation of
the vapor
Surface tension let the bubbles
implode
Implosion speed exceeds v1
Shock wave => cavitation
Critical heat flux - cavitation

## Slide 18
Critical heat flux

## Slide 19
Normal fluid cooling

## Slide 20
Thank you for your attention.

## Slide 21
Back-up slides
Values are good for ±10% for SVP

## Slide 22
Arp, Heat transport through helium II, 1970
Turbulent
Laminar

## Slide 23
Arp, Heat transport
Through helium II, 1970

## Slide 24
Cryoplant with mixed <2K cycle
Cryogenic distribution line
Indipendent Cryomodules

## Slide 25: Removal of bottom shield parts
Only top part left
“40-80 K” shield
Complete elimination not feasible

## Slide 26: Thermal shield at 5 K?
 | Full set of 5 K shield |  |  | Without 5 K lower shield |  | 
 | 2 K | 5 K | 40 K | 2 K | 5 K | 40 K
Static load, W | 1.13 | 9.70 | 93.8 | 1.14 | 8.10 | 95.9
Dynamic load, W | 10.02 | 7.06 | 83.0 | 10.02 | 7.06 | 83.0
Sum (static +dynamic) | 11.15 | 16.76 | 176.8 | 11.16 | 15.16 | 178.9
Work at 300 K, W | 7838.2 | 3317.5 | 2908.4 | 7845.3 | 3000.8 | 2942.9
Sum (2K+5K+40K), W | 14064 |  |  | 13789 |  | 
Power consumption kept constant !
Overall static/dynamic – Test data
P. Pierini – INFN

## Slide 27
Wound tube heat exchanger
ΔpVLP
= 41 Pa
= 0.41 mbar