## Slide 1: Cable Tray discussion
April 2022

## Slide 2: Fundamental Design Considerations
40 cable trays to be installed on the sides of the cryostat
Connections are limited to the support points at both the top and bottom of the cryostat
All materials to be LAr compatible and designed to withstand cryogenic operating temperatures
Each cable tray will need to support 8 cable bundles with a total cable mass of 360 kg per tray
Thermal contraction a significant design consideration
  Different material properties will lead to differential contraction between the cable tray structure and the supported cables
Top of Cryostat
Bottom of Cryostat

## Slide 3: FD2-VD Cryostat BDE Cold Cable Information
40 total cable trays required to supply 40 feedthroughs
  Each feedthrough will supply cabling to 2 bottom CRP assemblies (80 total)
A bottom CRP has 24 FEMBs (CE boxes)
  Each CE box will require 1 set of 25m long cables (power and data)
  1 cable tray will need to carry 48 sets of cable
    If divided into 8 bundles, each bundle would carry 6 sets of cable
    A cable bundle is approximately 40mm in diameter and has a mass of 45kg
Each cable tray will carry 8 bundles of cable
  360kg total mass of cables to be supported per cable tray

## Slide 4: FD2-VD Cryostat Cold Cable Information
Cable tray width dependent on layout of cables
  A single layer of cable bundles would likely need a 24” wide tray
    24” allows for almost 6” of space on each side of cable tray
    18” wide might be too narrow
  16” for BDE cables and 8” for any PD fibers?

## Slide 5: FD2-VD Cryostat Cold Cable Information
Cable thermal properties based upon experimental results
  A SAMTEC data cable was immersed in liquid nitrogen for 1 minute to simulate effect of thermal contraction
    Original cable length at room temperature (20°C): 45 3/4” [1162.0mm]
    Cable temperature at liquid nitrogen temperature (-196°C): 7/32” [5.6mm]
  Shrinkage Rate
    (0.21875”) / (45.75”) / {20°C - (-196°C)} = 2.2 e-5/°C
      (0.21875”) / (45.75”) = 0.00478 dL/L

## Slide 6: Cable Tray Material Considerations (Data from Cryogenic Material Properties Database, NIST)
304 Stainless Steel
  Linear expansion at 88K: -0.00272 dL/L

## Slide 7: Cable Tray Material Considerations (Data from Cryogenic Material Properties Database, NIST)
6061-T6 Aluminum
  Linear expansion at 88K: -0.00378 dL/L

## Slide 8: Cable Tray Installation Location
Does the cryostat membrane construction limit the maximum cable tray width?
  If we intend to fit the cable tray between the “knuckles” of the membrane, the tray will need to be made deeper to support all 8 cable bundles
    Max Clear gap is 26cm.
What are the limitations for cable placement?
  How far from the membrane can the cables be?
  What distance must the cables and cable tray maintain from the HV elements in the cryostat?
Maximum clear space
26cm

## Slide 9: Attachment of Cable Tray to Cryostat
Connections are limited to the support points at both the top and bottom of the cryostat
  360kg per cable tray for BDE cables plus PD cables and sensors.
  Connections will act as anchor points for thermal contraction
Cable tray width and placement to determine if one or two sets of attachment bolts are used

## Slide 10: Cable Tray Types: Ladder
Ladder cable trays typically used for vertical cabling applications
  Provide stronger cross section for load bearing
  Design may provide more options for interfacing with a PD sensor
Bracket could be designed to connect cable tray to cryostat support points
Manufacturers can provide expansion plates for thermal expansion/contraction

## Slide 11: Cable Tray Types: Wire Basket
Wire baskets not typically designed to handle large loads
  360kg cable load likely to be an issue with this type of cable tray
  Custom design might be needed
Custom solutions required to handle unique design challenges
  Attachment of wire basket to cryostat support points
  How to account for thermal contraction of wire basket due to LAr operating temperature

## Slide 12: Cable Tray Types: Truss
Potential alternative to standard commercially available cable tray designs
  Truss inner diagonals not typically designed to handle load
  Effects of thermal contraction would need to be thoroughly analyzed
Pipes provide an easy surface to clamp to for supporting PD sensors
Bracket could be designed to connect truss to cryostat support points
  Bolting plate options available at ends of truss could facilitate this attachment

## Slide 13: Cable Tray Budget
Total budget allotted for cable trays: $55,000
  $1,375.00 per cable tray (40 total trays required)
Major factors for cost:
  Cable tray material
  Cable tray size
  Attachment bracket design
  Design of thermal contraction elements