## Slide 1
Challenges in design, construction, and exploitation of Big Science Cryogenic Distribution Systems
Maciej Chorowski / Wroclaw Univ. of Science and Technology
PIP-II Technical Workshop
07/13/2022

## Slide 2
LHC
ITER
ILC
FAIR
XFEL
Helium cryogenics is a must in „Big Science”
ESS
PIP II

## Slide 3
Helium cryogenics and inventory in chosen projects

## Slide 4: Why Cryogenics ? - Critical current density of superconductors
LHC magnets ary cryostated with pressurized IIHe

## Slide 5: Why Cryogenics ? Optimization of operating temperature for superconducting RF cavity
BCS theory RBCS = (A w2 /T) exp (-B Tc/T)
For practical materials RS = RBCS + R0
Refrigeration (Carnot) Pa = P (Ta/T - 1)
 depending upon w and R0, optimum operating temperature for superconducting cavities
Niobium
Optimal operation temperaturę for Nb suepercondicting RF cavity is below 2 K.
RF Cavities are cryostated with saturated II He

## Slide 6: Why Supercritical Helium? Transport of refrigeration in large distributed cryogenic systems
To avoid two-phase flow helium is transported in supercritical state at the distance up to 3.3 km (LHC sector length)

## Slide 7: Phase diagram of helium
l line
„Big Science” cryogenic systems make extensive use of practically all thermodynamic states of cold helium:
Supercritical
Saturated He I
Saturated He II
Pressurized He II
Low pressure vapour

## Slide 8
Cryogenic Distribution System CDS
Connects a cryoplant with cryomodules, magnets, helium innventory tanks
Transfers helium in both directions
Allows cool down, cryostating, warm up a machine
Guarantees safe operation in all operating modes (including failure modes)
Main components of CDS are: transfer lines, valve boxes, jumper connections, warm piping systems

## Slide 9
Exemplary Cryogenic Distribution System – POLFEL
PolFEL (Polish Free Electron Laser) will be the first Free Electron Laser (FEL) facility operating in Poland and Eastern Europe.

## Slide 10
Simplified flow scheme of POLFEL Valve Box with corresponding T-s diagram Take notice of thermodynamic processes occuring in Valve Box/Cryomodule

## Slide 11: ESS Cryogenics System

## Slide 12: ESS Cryogenic Distribution System - WUST contribution to ESS
4-channel Cryogenic
Transfer Line (65m)
Cryogenic Distribution Line
with 30 valve boxes and 4 Aux lines
AIK 11.1 – Cryogenic Distribution for Elliptical Linac (CDS-EL)
AIK 11.3 – Cryogenic Distribution for Lund Test Stand2 (CDS-LTS2)
LTS2 Valve Box
4-channel Cryogenic
Transfer Line (65m)
Auxiliary Lines

## Slide 13
Accelerator Cryogenics
Distribution system delivers single
phase supercritical Helium at 4.5 K & 40 K
2 K helium produced at
each cryomodule
Sub atmospheric vapor pumped off
to cryoplant
4.5 K – 300 K cooling of couplers

## Slide 14
ESS Distribution Cryogenics System installed in the tunnel
Test stand allowing optimization of the main system

## Slide 15
Industrialization of the CDS valboxes production
The production rate accelerated from 6 monthes (first valve box) to three weeks (average)

## Slide 16: ITER cryogenic system – two temperature extremities meet
Central
Solenoid, Nb3Sn
Outer Intercoil Structure
Toroidal Field
Coil, Nb3Sn, 18
Poloidal Field
Coil, NbTi
Machine Gravity
Supports
Blanket Module
Vacuum
Vessel
Cryostat
Port Plug
(IC Heating)
Torus
Cryopump
Divertor
Cryolines
Cryodistribution
Cryolines
Cryodistribution
108 K
4,2 K

## Slide 17: ITER Cryogenic Distribution System - cooling loop of cable in conduit coils
Circulation of supercritical helium in CIC cables of ITER magnet coils

## Slide 18: ITER Cryogenic System
Main cryogenic
transfer lines
Helium and nitrogen liquefiers
in the cryoplant buildings
Cryodystribution
lines and boxes in the tokamak building

## Slide 19
ITER Cryogenic Distribution System in the tokamak building

## Slide 20
Challenges in design, construction and operation of CDS
Mechanical design compromising allowable heat balance with mechanical stability
Risk analysis and coping with failure modes
Industrialization of the production, CDS is the first system installed in the tunel
Vacuum sectorization
Control systems
And many others
Cryogenic Distribution System – definitely not „Just Piping”