## Slide 1
WG 4 - Cryogenic Distribution System
Thermal design of CDS components
PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
Jaroslaw Polinski
WUST, Wrocław, Poland
jaroslaw.polinski@pwr.edu.pl

## Slide 2: Content
Importance of the thermal insulations in cryogenic devices and systems
Cryogenic thermal insulation materials and systems
Multilayer Insulation (MLI) performance
Thermal Shields design review
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#2

## Slide 3: Compensation of the heat flux to insulated cold space
Scheme of the ideal refrigerator
Minimum work of the refrigerator:
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#3

## Slide 4: Minimum work of ideal refrigerator
Minimal work W to compensation of the heat flux Q0 in function of the cold temperature, environment temperature T=300K
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#4
For T0 = 4K -> W/Q0 ≈ 75 W/W
For T0 = 2K -> W/Q0 ≈ 150 W/W !!!

## Slide 5: Real efficiency of cryogenics refrigerators
% of Carnot cycle
Cooling capacity, (W)
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#5
Based on: Strobridge, T.R.: Cryogenic Refrigerators – an Updated Survey, NBS Tech Note 655, 1974.

## Slide 6: Cryogens evaporation losses due heat input
Volumetric cryogen losses due 1 W heat input
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#6

## Slide 7: Content
Importance of the thermal insulations in cryogenic devices and systems
Cryogenic thermal insulation materials and systems
Multilayer Insulation (MLI) performance
Thermal Shields design review
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#7

## Slide 8: Cryogenic thermal insultions
Close-cells foam
Thermal conductivity, W/m/K
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#8

## Slide 9: Thermal Shield concept
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#9

## Slide 10: TS optimal temperature (300 – 4K)
Tm_opt= 97K
Wtot / Wmin= 1.1
Tm= 116K
Tm= 80K
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#10

## Slide 11: Thermal Shield concept
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#11

## Slide 12: Thermal Shield concept
2nd Thernal Shield (between 77 – 4.2 K)
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#12

## Slide 13: Content
Importance of the thermal insulations in cryogenic devices and systems
Cryogenic thermal insulation materials and systems
Multilayer Insulation (MLI) performance
Thermal Shields design review
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#13

## Slide 14: Multilayer Insulation MLI
2 mm
Shield perforation hole
1.8 mm
1.6 mm
0.18 mm
Spacer
VACUUM
Environment – warm boundary
Insulated space – cold boundary
Shield perforation
Radiation shield
Spacer
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#14

## Slide 15: Multilayer Insulation MLI
Radiation shields:
Shield material: single or double side metal plated Mylar, Kapton, Dracon, material thickness: 5 – 75 mm
Pleating metals: Al, Ag, Cu, Au – layer thickness 0.05 do 0.1 mm (500 – 1000 Å)
Perforation: holes 1 – 3 mm diameter, perforation area: 0.1 – 0.3% of total area
Spacer material:
single/ double silky net
single/ double nylon net
glass fibres mats
Special cases:
Radiation shields are crinkled or dimpled and no spacer material is used
One shield side is metalized – no metalized side is concerned as low conductivity spacer and no additional spacer is used
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#15

## Slide 16: Multilayer Insulation MLI
Environment – warm boundary
Insulated space – cold boundary
Gas conduction
Radiation
Solid conduction
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#16

## Slide 17: Multilayer Insulation MLI
Main MLI insulation parameters:
Numbers of the shields
Shield reflecting metal layer material
Spacer material and structure
Vacuum level
Layers density
Methods of installation, (layer-by-layer, blankets/sub-blankets, seaming, butt-joining, spiral wrapping ect.)
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#17

## Slide 18: Compilation of the MLI experimental results
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#18
MLI config # | MLI description | Reference
1 | Lydall CRS – Aluminum foil 1145 - 0,7mm thickness + Cryotherm 1303 (microfiber glass non-woven binder free thermal spacer) | Senthil Kumar, A., Krishna Murthy, M.V., Jacob, S., Kasthurirengan, S. (2000). Thermal Performance of Multilayer Insulation Down to 4.2 K. Advances in Cryogenic Engineering. https://doi.org/10.1007/978-1-4615-4215-5_92
2 | Jehier IR 305 – Double aluminised Mylar (DAM) 6 mm thickness , 400Ao coating thickness on each side, perforation diameter 2mm at a pitch of 56mm + polyester tulle with weight of 5x103 kg/m2 | 
3 | NRC2 – Crinkled single side aluminized Mylar with thickness 6 mm | 
4 | IHI – 12mm dimpled, double aluminised Mylar, dimple diameter 2mm at a pitch of 6mm, dimple height 200mm | 
5 | DAM 12 mm, perforation 0.4%, 1.5 mm holes/nylon net 80 mm thickness | S. Jacob, S. Kasthurirengan, R. Karunanithi, Investigations into the thermal performance of multilayer insulation (300-77 K) Part 1: Calorimetric studies, Cryogenics,Volume 32, Issue 12, https://doi.org/10.1016/0011-2275(92)90328-8
6.1 | DAM 12mm/ glass fibres 76.2 mm – 63.28 layers/cm | S.L. Bapat, at all, Experimental investigations of multilayer, Insulation, August 1990 Cryogenics 30(8):711-719, DOI: 10.1016/0011-2275(90)90235-5
6.2 | DAM 12mm/ glass fibres 76.2 mm – 50 layers/cm | 
6.3 | DAM 12mm/ glass fibres 76.2 mm – 30 layers/cm | 
6.4 | DAM 12mm/ glass fibres 76.2 mm – 24.2 layers/cm | 
7 | NRC2 | Q.S. Shu, R.W. Fast, H.L. Hart, Heat flux from 277 to 77 K through a few layers of multilayer insulation, Cryogenics, Volume 26, Issue 12, https://doi.org/10.1016/0011-2275(86)90167-0
8 | Jehier IR 305 | Fesmire J.E,. Augustynowicz S.D, Darve C., Performance characterization of perforated multilayer insulation blankets, Proceedings of the 19h ICEC
9 | Single layer of DAM 25mm, 250A Al layer thickness | P. Lebrun et al., Investigation and qualification of thermal insulation systems between 80 K and 4.2 K. Cryogenics 32(ICMC Supplement), 44–47 (1992) 12
10 | DAM 25 mm, 250A/net 30 mm, 4x5 mm x mm | 
11 | DAM 6 mm, 400A /net 6 mm | 
12 | DAM 8 mm, 230A/CRYOTHERM 2330 60 mm | Benda V e al., Qualification of multilayer insulation systems between 80 K and 4.2 K, Proc. Cryogenics 2000, International Institute of Refrigeration
13 | DAM 8 mm, 230A/SYNTRA 5507 90 mm | 
14 | Al 11 mm, 230A/CRYOTHERM 2330 60 mm | 

## Slide 19: Compilation of the MLI experimental results
Temperature range: 300 – 77K, vacuum condition: vary, residual gas: N2
MLI conf #5
MLI conf #12
MLI conf #8
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#19

## Slide 20: Compilation of the MLI experimental results
Temperature range: 300 – 77K, vacuum condition: very good
#1
#2
#3
#4
#5
#6.3
#7
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#20

## Slide 21: MLI performance for 300-80K temperature range
J.E. Fesmire, W.L. Johnson, Cylindrical cryogenic calorimeter testing of six types of multilayer insulation systems, Cryogenics 89 (2018) 58–75
https://doi.org/10.1016/j.cryogenics.2017.11.004
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#21

## Slide 22: Self compression of MLI at horizontal cylinders
T.Ohmori, Thermal performance of multilayer insulation around a horizontal cylinder, Cryogenics 45 (2005) 725-732
https://doi.org/10.1016/j.cryogenics.2005.06.009
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#22

## Slide 23: Compilation of the MLI experimental results
Temperature range: 300 – 77K, vacuum condition: very good
#6.4
#6.3
#6.2
#6.1
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#23

## Slide 24: Compilation of the MLI experimental results
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#24
B. Deng et al., Study of the thermal performance of multilayer insulation used in cryogenic transfer lines, Cryogenics 100 (2019) 114–122
115, https://doi.org/10.1016/j.cryogenics.2019.01.005

## Slide 25: Compilation of the MLI experimental results
Temperature range: 77 – 4.2 K, vacuum condition: vary, residual gas: He
#10
#11
#12
#14
#13
#9

## Slide 26: Compilation of the MLI experimental results
Temperature range: 77 – 4.2 K, vacuum condition: very good
#1
#2
#3
#4
#10
#11
#12
#13
#14
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#26

## Slide 27: Compilation of the MLI experimental results
T cold = 4.2 K, T hot : vary, vacuum condition: very good
V. Venturi, Thermodynamic and technological optimization of complex cryogenic insulation systems, PhD Thesis at WUST and CERN
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#27

## Slide 28: MLI durng vacuum ventilation with atmospheric air (failure event)
Heat transfer to the helium vessel in case of vacuum vessel sudden ventilation with atmospheric air
W. Lehman and G. Zahn, Safety aspects for LHe cryostats and LHe transport containers, Kernforschungzentrum Karlsruhe, Institut fur Technische Physik, 7500 Karlsruhe, Germany.
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#28

## Slide 29: MLI Summary
60 – 80K temperature surfaces against 300K are usually covered with 30 – 50 layers of MLI
  Heat transfer is low enough
  Higher number of MLI layers does not significantly reduce the heat flux, but increases the production costs (material, pumping time, outgassing)
  Large number of MLI layers on a horizontal surface can lead to MLI self-compression and degradation of insulation performance
4K temperature surfaces against 80K are usually covered with 10 layers of MLI (LHC case)
  Heat transfer is low enough
  Higher number of MLI layers can increase the heat flux
  Heat loads are relatively low in case of the sudden vacuum lost case
The MLI density shall be not larger than 30 layers/cm.
Vacuum pressure shall be lower than 10-3 Pa for 300 – 80K case and lower than 10-4 Pa for 4 – 80 K case
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#29

## Slide 30: Content
Importance of the thermal insulations in cryogenic devices and systems
Cryogenic thermal insulation materials and systems
Multilayer Insulation (MLI) performance
Thermal Shields design review
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#30

## Slide 31: LHC Thermal Shield design
Cross-section of the LHC
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#31

## Slide 32: XFEL Cryo system scheme

## Slide 33: XFEL cryomodule cross section
2.2 K forward DN40
40 K forward
2 K 2-phase 76 mm
cavity
2 K return DN300
80 K return DN65
8 K return DN65
RF main coupler
magnet current feedthrough
5 K forward DN65
5 K shield
70 K shield
2K Bypass DN32
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#33

## Slide 34: XFEL cryomodule Thermal Shield

## Slide 35: 4.5K Thermal Shield for 2K surfaces?
XFEL
Cryomodule
ILC
Cryomodule
In the ILC CM the upper TS parts are retained to cool the intercepts of input couplers, current leads, HOM couplers, HOM absorber and RF cables, and to provide mechanical support to the intercepts.
In an addition, ILC cooling scheme is slightly modified to cool intercepts at lower temperature levels (46K and 66K instead of 54K and 74K, respectively)
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#35

## Slide 36: 4.5K Thermal Shield for 2K surfaces?
P. Lebruna et al., Does one need a 4.5 K screen in cryostats of superconducting accelerator devices operating in superfluid helium?, AIP Conference Proceedings 1573, 245 (2014); https://doi.org/10.1063/1.4860708
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#36

## Slide 37: 4.5K Thermal Shield for 2K surfaces?
PolFEL
Cryomodule
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#37

## Slide 38: XATL1 Transfer Line (XFEL AMTF)
Vacuum vessel (Austenitic Stainless steel 304, 1.4301)
Process pipes (Austenitic Stainless steel 304L, 1.4306)
Radiation shield
(Aluminium alloy Al6060)
Sliding support
(Epoxy G-10)
Spacer
(Glassboard)
Thermal bridge
between radiation shield and 80 K process pipe
(Copper)
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#38

## Slide 39: XATL1 Transfer Line (XFEL AMTF)
Aluminium thermal shield, ø300x4 mm
Thermal bridge 24 pcs.
Stainless steel cooling pipe, ø48.3x2 mm
Aluminium block welded to the aluminium pipe
Copper wires knead from both sides by press
Copper block tied to the stainless steel pipe
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#39

## Slide 40: XATC Test Cryosat (XFEL AMTF)
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#40

## Slide 41: ESS CDS-EL Valve Box
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#41

## Slide 42: ESS CDS-EL (ESS, Lund, Sweden)
Aluminium TS
Copper flexible connector bolted to aluminium pipe
Copper clamps bolted to the cooling pipe
Aluminium cover
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#42

## Slide 43: FAIR SIS100 BPL - prototype module
Aluminum block with the flexible strands is welded to Al thermal shield
Copper block with the flexible strands is bolted to stainless steel tube
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#43

## Slide 44: FAIR SIS100 BPL - prototype module commissioning tests results
80K
Broken
81K
81K
TS_Return – 60.4K
Theoretical thermal conductivity
= 1.07 W/K
A – total cross section of the Cu strands – 12 x 16 mm2
L – strand length – 90 mm
k – thermal cond. of Cu – 500 W/mK
Real thermal conductivity:
TS return line T=60.4K
TS temp T=80K
Measured heat flux to TS – 49.2W
No of thermal connections – 6
qreal= 0.425 W/K
Measurement results Curtesy GSI
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#44

## Slide 45: Which copper for TS and thermal couplers? OFE or ETP?
For radiation shield and nitrogen purposes
thermal conductivity OFE ≈ ETP
4K
70K
For helium purposes
thermal conductivity OFE >> ETP
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#45

## Slide 46: Thermal shield design summary
Extruded Thermal Shield
  Excellent thermal conduction,
  For cryogenic systems with length above of several hundred meters,
  Potential problem with production certification
  Potential problems with bi-metalic joints
  Dedicated design that cannot be easily used in different projects
„Tailored” Thermal Shields
  More complex in assembly (thermal coupling) – no issue in unit production,
  Difference in thermal contraction between the process pipe and thermal shield materials need to be accounted in the design,
  Components readily available in the market,
  Sophisticated shapes are possible.
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#46

## Slide 47
Thank you for your attention
J. Polinski, Thermal design of CDS components, PIP II Technical Workshop, FNAL/Remotely, 12-14 of July 2022
#47