## Slide 1
Matt Micheli on behalf of Grounding team
(Bagby, Harris, Mastro)
2x2 @LArTF Electronics Integration
June 30, 2022
Dune-ND
ArgonCube 2x2 @ LArTF
Low-Noise AC Power Grounding Status

## Slide 2: Outline
Low-Noise AC Power System Design
Issue Identification
Mitigation Efforts
Plans

## Slide 3: Low Noise AC Power Distribution Proximity
NOT INSTALLED

## Slide 4: Simple graphic of system
XO
4 Conduits
PP B
XFMR B
SI
CT
Detector Safety
Ground cable
XO
~12 Conduits
PP A
XFMR A
SI
CT
Detector Safety
Ground cable
uBooNE Power
2x2 Power

## Slide 5: The Ground Fault
XO
4 Conduits
PP B
XFMR B
SI
CT
Detector Safety
Ground cable
XO
~12 Conduits
PP A
XFMR A
SI
CT
Detector Safety
Ground cable
uBooNE Power
2x2 Power
Impedance Monitor
When impedance monitor was initially powered on, a 10Ω ground fault was discovered

## Slide 6: Reality of mission

## Slide 7: Conduit Route: Around the wall and up

## Slide 8: Conduit Route: Across to east side wall and down

## Slide 9: Issue Identification: 10 W short
XO
4 Conduits
PP B
XFMR B
SI
CT
Detector Safety
Ground cable
XO
~10 Circuits
PP A
XFMR A
SI
CT
Detector Safety
Ground cable
uBooNE Power
2x2 Power
Detector Safety ground cable was the first to be lifted and tested
No problems were found with cable, no changes to impedance monitor
Cable was then lifted at CT/SI box, no changes occurred

## Slide 10: Issue Identification: 10 W short
XO
4 Conduits
PP B
XFMR B
SI
CT
Detector Safety
Ground cable
XO
~10 Circuits
PP A
XFMR A
SI
CT
Detector Safety
Ground cable
uBooNE Power
2x2 Power
Conduits and ground lifted at panel
Conduits and wireway became isolated

## Slide 11: Problem Locations

## Slide 12: Problem Locations

## Slide 13: Issue Identification: 10 W short
XO
4 Conduits
PP B
XFMR B
SI
CT
Detector Safety
Ground cable
XO
~10 Circuits
PP A
XFMR A
SI
CT
Detector Safety
Ground cable
uBooNE Power
2x2 Power
Best option to verify was to lift at the CT

## Slide 14: Mitigation Efforts
Panel B
Note: Panel B was lifted from CT prior to work
Panel A
CT Lift Spot

## Slide 15: Testing the results
Success!
  Impedance monitor was turned on and was working as intended
Detector Safety ground cable, CT/SI box, conduits, and wireway grounds were reconnected to verify isolation
  Impedance monitor continued working as intended

## Slide 16: Plans
While Impedance monitor is now functional, we need to isolate the conduit run so that Panel A can properly function
Install fiberglass unistrut at 3 locations
  Procedure composed
  HA Submitted and approved
  Work is commencing today
Quick verification of Impedance monitor operation
Arrange ORC review
  Many conduit and wiring connections were lifted to find problem.
  All need to be re-reviewed before powering system.
Conduct characterization measurement
Release system to Operations