## Labor
LBNF EXTRACTION LINE
MI-10 Q-103 thru Q-107 LCW & BUS RETROFIT
LABOR ESTIMATE
|  | FERMI |  | TRADES
| TASK | LABOR |  | LABOR |  | NOTES
|  | Type | Hours | Type | Hours
FINAL DESIGN
| Final Design | Fluids Eng'r | 200
|  | Magnet Eng'r | 24
|  | Elec. Eng'r | 24
|  | Drafter/Designer | 400
| Final Design Review | Fluids Eng'r | 60
|  | Magnet Eng'r | 16
|  | Elec. Eng'r | 16
|  | Drafter/Designer | 100
|  | Machine Eng/Phys | 60
| Installation | Fluids Eng'r | 120
|  | Magnet Eng'r | 20
|  | Elec. Eng'r | 20
|  | Drafter/Designer | 40
| Installation Document Review & As-Builts | Fluids Eng'r | 40
|  | Magnet Eng'r | 4
|  | Elec. Eng'r | 4
|  | Drafter/Designer | 60
PIPE & BUS REMOVAL
Global LCW Pipe:
| Shut down MI LCW system, isolate, drain and prep for long term shutdown | Fluids Tech | 48 |  |  | 3 techs x 2 days
| Disconnect dipoles, quads, remove hoses, flags, move to storage | Fluids Tech | 48 |  |  | 3 techs x 2 days
| Stage and prep for Q100 tunnel work - LCW & bus removal |  |  | Pipfitter | 16 | 2 pf x 1 days
| Mark & cut LCW pipe, move to storage |  |  | Pipfitter | 80 | 2 pf x 5 days
Quadrupole Bus:
| Mark & cut quad bus, move to storage |  |  | Pipfitter | 120 | min 6 man crew, DS alcove walll @ Q-103 thru D-107-1 & -2, 8 lbs/ft ttl ~ 550', ~ 4600 lbs
| Remove header & bus wall brackets, move to storage |  |  | Pipfitter | 16
Dipole Bus:
| Remove dipole bus & brackets, move to storage |  |  | Pipfitter | 120 | min 6 man crew, Q-103 thru Q-107, 15 lbs/ft, 5 pair in sets @ ~ 600 lbs/set
MI-14 LCW & Fluorinert Pipe:
| Shut down MI-14 Fluorinert system, isolate, drain both LCW and Fuorinert sides of system | Fluids Tech | 48 |  |  | 3 techs x 2 days
|  | Kicker Tech | 8 |  |  | 1 tech x 1 day
| Empty MI-14 Girardi box, and penetrations to Q-105 | Fluids Tech | 16 |  |  | 2 days, cubic yards of poly beads to deal with
|  | Rad Tech | 16
|  | Bead Removal Crew | 32
| Stage and prep for Q-105 & MI-14 work - LCW & Fluorinert removal |  |  | Pipfitter | 16 | 2 pf x 1 day
| Mark & cut pipes @ Q-105 |  |  | Pipfitter | 8 | 2 pf x 0.5 day
| Mark & cut pipes @ MI-14 |  |  | Pipfitter | 8 | 2 pf x 0.5 day
| Extract pipes from top of Girardi box thru MI-14, move to storage | Fluids Tech |  | Pipfitter | 80 | all 4 runs are around 50' length, 2 each at about a 40 degree angle thru the penetration, with spiders, and barely fit installation inside of roof by bending pipe what it would sag by weight
| Close & protect all open ends to systems | Fluids Tech | 16 | Pipfitter
| Clean up, remove equipment, all work shelved |  | 4 | Pipfitter | 16
| Task Manager for above | Fluids Tech | 120 |  |  | Full length of construction + prep / wrap up
ENCLOSURE UTILITIES PREP FOR TO REINSTALL
Beneficial occupancy, all survey & layout work complete
| Move, lower, relocate grounding strap on outer enclosure (magnet) wall bottom |  |  | Electrician | 32 | 2 elec x 2 days
| Lower cable trays in center of overhead to enable installation of LCW crossover piping |  |  | Electrician | 64 | 4 elec x 2 days
| Move, lower, relocate lighting and conduits on Aisle side |  |  | Electrician | 80 | 2 elec x 5 days
| Raise & return cable trays in center of overhead to proper elevation |  |  | Electrician | 64 | 4 elec x 2 days
PIPE & BUS INSTALLATION
Global LCW Pipe:
| Stage and prep and layout for Q100 tunnel work - LCW & bus installation |  | 24 | Pipfitter |  | 3 pf x 1 day, placement of manifolds and taps, valves, on upper aisle side
| Retrieve header piping, brackets, etc from storage and/or delivery |  | 24 | Pipfitter |  | 3 pf x 1 day
| Remove, modify, and reinstall manifolds w/ crossovers |  | 160 | Pipfitter |  | 2 pf x 10 day
| Install header pipe hangers on aisle side |  | 32 | Pipfitter |  | 2 pf x 2 day
| Install header piping for Q-107 cross-over |  | 80 | Pipfitter |  | 2 pf x 5 day
| Install header piping from Q-103 alcove to Q-107 cross-over |  | 240 | Pipfitter |  | 3 pf x 10 day
| Reinstall all hoses, brackets, any misc. | Fluids Tech | 32 |  |  | 2 techs x 2 days
| Fill & test system headers | Fluids Tech | 16 |  |  | 2 techs x 1 day - DO NOT FILL UNTIL READY! hydrostatic test not required nor advisable
| Bring system to operational status | Fluids Tech | 16 |  |  | 2 techs x 1 day
| Valve in quad cells | Fluids Tech | 8 |  |  | 2 techs x 0.5 days
| Task Manager for above | Fluids Tech | 240 |  |  | 30 DAYS Full length of construction + prep / wrap up
MI-14 Fluorinert & LCW Pipe:
| Inspect & prep penetrations between MI-14 to Q-105 for piping fit | Fluids Eng'r | 8
|  | Drafter/Designer | 8
|  | Task Manager | 12
| Retrieve & stage LCW and Fluorinert piping, brackets, etc from storage and/or delivery | Fluids Tech | 8 | Pipfitter | 8
| Reinstall LCW and Fluorinert lines through penetrations to MI-14 system |  |  | Pipfitter | 120 | 3 pf x 5 Day
| Install Fluorinert lines to kickers |  |  | Pipfitter | 32 | 2 pf x 2 day
| Installl modified piping runs across ceiling, similar to manifolds |  |  | Pipfitter | 32 | 2 pf x 2 day
| Install LCW hoses to header | Fluids Tech | 4
| Fill & test MI-14 skid system | Fluids Tech | 4
| Refill MI-14 Girardi box, and penetrations to Q-105 | Fluids Tech | 8 |  |  | cubic yards of poly beads to deal with
|  | Rad Tech | 8
|  | Bead Refill Crew | 24
z | Reinstall all hoses, brackets, any misc. | Fluids Tech | 8
| Fill & test system headers, Valve in kickers | Fluids Tech | 8 |  |  | NOT UNTIL READY! hydrostatic test not required nor a good idea
|  | Kicker Tech | 8
| Task Manager for above | Fluids Tech | 120 |  |  | Full length of construction + prep / wrap up
| Primary Beamline LCW Fill Line Pipe: |  |  |  |  | New line, no removal necessary
| Install PBE fill line piping at Q-105 cross-over |  |  | Pipfitter | 32
| Install all hoses, brackets, any misc. | Fluids Tech | 8
| Fill & test system line | Fluids Tech | 4 |  |  | NOT UNTIL READY! hydrostatic test not required nor a good idea
| Task Manager for above | Fluids Tech | 24 |  |  | Full length of construction + prep / wrap up
Quadrupole Bus:
| Retrieve & stage quad bus, brackets, etc from storage and/or delivery | Fluids Tech | 8 | Pipfitter | 8
| Reinstall quadrupole bus & hangers in new location |  |  | Pipfitter / Electrician | 480 | 6 x 10 day, min 6 man crew, DS alcove walll @ Q-103 thru D-107-1 & -2, 8 lbs/ft , ttl ~ 550', ~ 4600 lbs
| On-site fab & braze of 7/8" bus connection x 2 at each quad | Fluids Tech | 32 |  |  | Often lab insisted to be Fermi techs for magnet connections
| Task Manager for above | Fluids Tech | 96 |  |  | Full length of construction + prep / wrap up
| Dipole Bus: |  |  |  |  | min 6 man crew, Q-103 thru Q-107, 15 lbs/ft, 5 pair in sets @ ~ 600 lbs/set; requires sync w/ magnet installation
| Retrieve dipole bus, flags, brackets, etc from storage and/or delivery | Fluids Tech | 8 |  |  | 2 techs x .5 day
| Reinstall dipole bus & hangers in existing location at each quad |  |  | Pipfitter / Electrician | 200 | 5 crew x 5 day
| Reinstall & certify flags | Elec. Tech | 16 |  |  | 2 techs x 2 days
| Reinstall hoses | Fluids Tech | 16
| Task Manager for above | Fluids Tech | 40 |  |  | Full length of construction + prep / wrap up
| LABOR HOUR TOTALS - FERMILAB | TYPE | HOURS
|  | Bead Crew | 56
|  | Drafter/Designer | 608
|  | Elec. Eng'r | 64
|  | Elec. Tech | 32
|  | Fluids Eng'r | 428
|  | Fluids Tech | 856
|  | Machine Eng/Phys | 60
|  | Magnet Eng'r | 64
|  | Rad Tech | 24
| LABOR HOUR TOTALS - TRADE | SOLO CREW | COMBINED CREW - 3 | TOTAL |  | NOTES ON TRADES:
| Pipfitter - note 1 | 232 | 240 | 472 |  | 1 – PIPEFITTER SOLO CREW is primarily pipe work
| Electrician - note 2 | 240 | 440 | 680 |  | 2 – ELECTRICIAN SOLO CREW is estimate for Utilities work, refer to C. Gatusso work for more accurate values
3 – COMBINED CREW is for the mixed crew for Buswork
REFER TO C. GATTUSO ESTIMATE,
BOE Report 131.NSCFB.03.05.05_Installation Coordination

## Labor Tallies - Fermi
|  | Bead Crew | 24
|  | Bead Crew | 32
|  |  | 56 | TOTAL
|  | Drafter/Designer | 400
|  | Drafter/Designer | 100
|  | Drafter/Designer | 40
|  | Drafter/Designer | 60
|  | Drafter/Designer | 8
|  |  | 608 | TOTAL
|  | Elec. Eng'r | 24
|  | Elec. Eng'r | 16
|  | Elec. Eng'r | 20
|  | Elec. Eng'r | 4
|  |  | 64 | TOTAL
| Reinstall & certify flags | Elec. Tech | 16 |  |  | 2 techs x 2 days
|  | Kicker Tech | 8 |  |  | 1 tech x 1 day
|  | Kicker Tech | 8
|  |  | 32 | TOTAL
| Final Design | Fluids Eng'r | 200
| Final Design Review | Fluids Eng'r | 60
| Installation | Fluids Eng'r | 120
| Installation Document Review & As-Builts | Fluids Eng'r | 40
| Inspect & prep penetrations between MI-14 to Q-105 for piping fit | Fluids Eng'r | 8
|  |  | 428 | TOTAL
| Shut down MI LCW system, isolate, drain and prep for long term shutdown | Fluids Tech | 48 |  |  | 3 techs x 2 days
| Disconnect dipoles, quads, remove hoses, flags, move to storage | Fluids Tech | 48 |  |  | 3 techs x 2 days
| Shut down MI-14 Fluorinert system, isolate, drain both LCW and Fuorinert sides of system | Fluids Tech | 48 |  |  | 3 techs x 2 days
| Empty MI-14 Girardi box, and penetrations to Q-105 | Fluids Tech | 16 |  |  | 2 days, cubic yards of poly beads to deal with
| Extract pipes from top of Girardi box thru MI-14, move to storage | Fluids Tech |  | Pipfitter | 80 | all 4 runs are around 50' length, 2 each at about a 40 degree angle thru the penetration, with spiders, and barely fit installation inside of roof by bending pipe what it would sag by weight
| Close & protect all open ends to systems | Fluids Tech | 16 | Pipfitter
| Task Manager for above | Fluids Tech | 120 |  |  | Full length of construction + prep / wrap up
| Reinstall all hoses, brackets, any misc. | Fluids Tech | 32 |  |  | 2 techs x 2 days
| Fill & test system headers | Fluids Tech | 16 |  |  | 2 techs x 1 day - DO NOT FILL UNTIL READY! hydrostatic test not required nor advisable
| Bring system to operational status | Fluids Tech | 16 |  |  | 2 techs x 1 day
| Valve in quad cells | Fluids Tech | 8 |  |  | 2 techs x 0.5 days
| Task Manager for above | Fluids Tech | 240 |  |  | 30 DAYS Full length of construction + prep / wrap up
| Retrieve & stage LCW and Fluorinert piping, brackets, etc from storage and/or delivery | Fluids Tech | 8 | Pipfitter | 8
| Install LCW hoses to header | Fluids Tech | 4
| Fill & test MI-14 skid system | Fluids Tech | 4
| Refill MI-14 Girardi box, and penetrations to Q-105 | Fluids Tech | 8 |  |  | cubic yards of poly beads to deal with
| Reinstall all hoses, brackets, any misc. | Fluids Tech | 8
| Fill & test system headers, Valve in kickers | Fluids Tech | 8 |  |  | NOT UNTIL READY! hydrostatic test not required nor a good idea
| Task Manager for above | Fluids Tech | 120 |  |  | Full length of construction + prep / wrap up
| Install all hoses, brackets, any misc. | Fluids Tech | 8
| Fill & test system line | Fluids Tech | 4 |  |  | NOT UNTIL READY! hydrostatic test not required nor a good idea
| Task Manager for above | Fluids Tech | 24 |  |  | Full length of construction + prep / wrap up
| Retrieve & stage quad bus, brackets, etc from storage and/or delivery | Fluids Tech | 8 | Pipfitter | 8
| On-site fab & braze of 7/8" bus connection x 2 at each quad | Fluids Tech | 32 |  |  | Often lab insisted to be Fermi techs for magnet connections
| Task Manager for above | Fluids Tech | 96 |  |  | Full length of construction + prep / wrap up
| Retrieve dipole bus, flags, brackets, etc from storage and/or delivery | Fluids Tech | 8 |  |  | 2 techs x .5 day
| Reinstall hoses | Fluids Tech | 16
|  | Task Manager | 12
| Task Manager for above | Fluids Tech | 40 |  |  | Full length of construction + prep / wrap up
|  |  | 856 | TOTAL
|  | Machine Eng/Phys | 60
|  |  | 60 | TOTAL
|  | Magnet Eng'r | 24
|  | Magnet Eng'r | 16
|  | Magnet Eng'r | 20
|  | Magnet Eng'r | 4
|  |  | 64 | TOTAL
|  | Rad Tech | 16
|  | Rad Tech | 8
|  |  | 24 | TOTAL
| LABOR TOTALS - FERMILAB | Bead Crew | 56
|  | Drafter/Designer | 608
|  | Elec. Eng'r | 64
|  | Elec. Tech | 32
|  | Fluids Eng'r | 428
|  | Fluids Tech | 856
|  | Machine Eng/Phys | 60
|  | Magnet Eng'r | 64
|  | Rad Tech | 24
| TASK | LABOR |  | LABOR |  | NOTES
|  | FERMI |  | TRADES
|  | Type | Hours | Type | Hours
LBNF EXTRACTION LINE
MI-10 Q-103 thru Q-107 LCW & BUS RETROFIT
LABOR ESTIMATE
FINAL DESIGN
PIPE & BUS REMOVAL
Global LCW Pipe:
| Stage and prep for Q100 tunnel work - LCW & bus removal |  |  | Pipfitter | 16 | 2 pf x 1 days
| Mark & cut LCW pipe, move to storage |  |  | Pipfitter | 80 | 2 pf x 5 days
Quadrupole Bus:
| Mark & cut quad bus, move to storage |  |  | Pipfitter | 120 | min 6 man crew, DS alcove walll @ Q-103 thru D-107-1 & -2, 8 lbs/ft ttl ~ 550', ~ 4600 lbs
| Remove header & bus wall brackets, move to storage |  |  | Pipfitter | 16
Dipole Bus:
| Remove dipole bus & brackets, move to storage |  |  | Pipfitter | 120 | min 6 man crew, Q-103 thru Q-107, 15 lbs/ft, 5 pair in sets @ ~ 600 lbs/set
MI-14 LCW & Fluorinert Pipe:
| Stage and prep for Q-105 & MI-14 work - LCW & Fluorinert removal |  |  | Pipfitter | 16 | 2 pf x 1 day
| Mark & cut pipes @ Q-105 |  |  | Pipfitter | 8 | 2 pf x 0.5 day
| Mark & cut pipes @ MI-14 |  |  | Pipfitter | 8 | 2 pf x 0.5 day
| Clean up, remove equipment, all work shelved |  | 4 | Pipfitter | 16
ENCLOSURE UTILITIES PREP FOR TO REINSTALL
Beneficial occupancy, all survey & layout work complete
| Move, lower, relocate grounding strap on outer enclosure (magnet) wall bottom |  |  | Electrician | 32 | 2 elec x 2 days
| Lower cable trays in center of overhead to enable installation of LCW crossover piping |  |  | Electrician | 64 | 4 elec x 2 days
| Move, lower, relocate lighting and conduits on Aisle side |  |  | Electrician | 80 | 2 elec x 5 days
| Raise & return cable trays in center of overhead to proper elevation |  |  | Electrician | 64 | 4 elec x 2 days
z
PIPE & BUS INSTALLATION
Global LCW Pipe:
| Stage and prep and layout for Q100 tunnel work - LCW & bus installation |  | 24 | Pipfitter |  | 3 pf x 1 day, placement of manifolds and taps, valves, on upper aisle side
| Retrieve header piping, brackets, etc from storage and/or delivery |  | 24 | Pipfitter |  | 3 pf x 1 day
| Remove, modify, and reinstall manifolds w/ crossovers |  | 160 | Pipfitter |  | 2 pf x 10 day
| Install header pipe hangers on aisle side |  | 32 | Pipfitter |  | 2 pf x 2 day
| Install header piping for Q-107 cross-over |  | 80 | Pipfitter |  | 2 pf x 5 day
| Install header piping from Q-103 alcove to Q-107 cross-over |  | 240 | Pipfitter |  | 3 pf x 10 day
MI-14 Fluorinert & LCW Pipe:
| Reinstall LCW and Fluorinert lines through penetrations to MI-14 system |  |  | Pipfitter | 120 | 3 pf x 5 Day
| Install Fluorinert lines to kickers |  |  | Pipfitter | 32 | 2 pf x 2 day
| Installl modified piping runs across ceiling, similar to manifolds |  |  | Pipfitter | 32 | 2 pf x 2 day
| Primary Beamline LCW Fill Line Pipe: |  |  |  |  | New line, no removal necessary
| Install PBE fill line piping at Q-105 cross-over |  |  | Pipfitter | 32
Quadrupole Bus:
| Reinstall quadrupole bus & hangers in new location |  |  | Pipfitter / Electrician | 480 | 6 x 10 day, min 6 man crew, DS alcove walll @ Q-103 thru D-107-1 & -2, 8 lbs/ft , ttl ~ 550', ~ 4600 lbs
| Dipole Bus: |  |  |  |  | min 6 man crew, Q-103 thru Q-107, 15 lbs/ft, 5 pair in sets @ ~ 600 lbs/set; requires sync w/ magnet installation
| Reinstall dipole bus & hangers in existing location at each quad |  |  | Pipfitter / Electrician | 200 | 5 crew x 5 day
REFER TO C. GATTUSO ESTIMATE,
BOE Report 131.NSCFB.03.05.05_Installation Coordination

## Labor Tallies - Trades
| Move, lower, relocate grounding strap on outer enclosure (magnet) wall bottom |  |  | Electrician | 32 | 2 elec x 2 days
| Lower cable trays in center of overhead to enable installation of LCW crossover piping |  |  | Electrician | 64 | 4 elec x 2 days
| Move, lower, relocate lighting and conduits on Aisle side |  |  | Electrician | 80 | 2 elec x 5 days
| Raise & return cable trays in center of overhead to proper elevation |  |  | Electrician | 64 | 4 elec x 2 days
[5 empty] | 240 | TOTAL
| Stage and prep for Q100 tunnel work - LCW & bus removal |  |  | Pipfitter | 16 | 2 pf x 1 days
| Mark & cut LCW pipe, move to storage |  |  | Pipfitter | 80 | 2 pf x 5 days
| Mark & cut quad bus, move to storage |  |  | Pipfitter | 120 | min 6 man crew, DS alcove walll @ Q-103 thru D-107-1 & -2, 8 lbs/ft ttl ~ 550', ~ 4600 lbs
| Remove header & bus wall brackets, move to storage |  |  | Pipfitter | 16
| Remove dipole bus & brackets, move to storage |  |  | Pipfitter | 120 | min 6 man crew, Q-103 thru Q-107, 15 lbs/ft, 5 pair in sets @ ~ 600 lbs/set
| Stage and prep for Q-105 & MI-14 work - LCW & Fluorinert removal |  |  | Pipfitter | 16 | 2 pf x 1 day
| Mark & cut pipes @ Q-105 |  |  | Pipfitter | 8 | 2 pf x 0.5 day
| Mark & cut pipes @ MI-14 |  |  | Pipfitter | 8 | 2 pf x 0.5 day
| Extract pipes from top of Girardi box thru MI-14, move to storage | Fluids Tech |  | Pipfitter | 80 | all 4 runs are around 50' length, 2 each at about a 40 degree angle thru the penetration, with spiders, and barely fit installation inside of roof by bending pipe what it would sag by weight
| Close & protect all open ends to systems | Fluids Tech | 16 | Pipfitter
| Clean up, remove equipment, all work shelved |  | 4 | Pipfitter | 16
| Stage and prep and layout for Q100 tunnel work - LCW & bus installation |  | 24 | Pipfitter |  | 3 pf x 1 day, placement of manifolds and taps, valves, on upper aisle side
| Retrieve header piping, brackets, etc from storage and/or delivery |  | 24 | Pipfitter |  | 3 pf x 1 day
| Remove, modify, and reinstall manifolds w/ crossovers |  | 160 | Pipfitter |  | 2 pf x 10 day
| Install header pipe hangers on aisle side |  | 32 | Pipfitter |  | 2 pf x 2 day
| Install header piping for Q-107 cross-over |  | 80 | Pipfitter |  | 2 pf x 5 day
| Install header piping from Q-103 alcove to Q-107 cross-over |  | 240 | Pipfitter |  | 3 pf x 10 day
| Retrieve & stage LCW and Fluorinert piping, brackets, etc from storage and/or delivery | Fluids Tech | 8 | Pipfitter | 8
| Reinstall LCW and Fluorinert lines through penetrations to MI-14 system |  |  | Pipfitter | 120 | 3 pf x 5 Day
| Install Fluorinert lines to kickers |  |  | Pipfitter | 32 | 2 pf x 2 day
| Installl modified piping runs across ceiling, similar to manifolds |  |  | Pipfitter | 32 | 2 pf x 2 day
| Install PBE fill line piping at Q-105 cross-over |  |  | Pipfitter | 32
| Retrieve & stage quad bus, brackets, etc from storage and/or delivery | Fluids Tech | 8 | Pipfitter | 8
[5 empty] | 232 | TOTAL
| Reinstall quadrupole bus & hangers in new location (2 pf + 4 elec minimum) |  |  | Pipfitter / Electrician | 480 | 6 x 10 day, min 6 man crew, DS alcove walll @ Q-103 thru D-107-1 & -2, 8 lbs/ft , ttl ~ 550', ~ 4600 lbs
| Reinstall dipole bus & hangers in existing location at each quad (2 pf + 4 elec minimum) |  |  | Pipfitter / Electrician | 200 | 5 crew x 5 day
[5 empty] | 680 | TOTAL
| SPLIT TOTAL BETWEEN PF & ELEC |  |  | Pipfitter | 240
|  |  |  | Electrician | 440
| LABOR TOTALS - TRADES |  |  | Pipfitter | 472
|  |  |  | Electrician | 680
| TASK | LABOR |  | LABOR |  | NOTES
|  | FERMI |  | TRADES
|  | Type | Hours | Type | Hours
LBNF EXTRACTION LINE
MI-10 Q-103 thru Q-107 LCW & BUS RETROFIT
LABOR ESTIMATE
FINAL DESIGN
| Final Design | Fluids Eng'r | 200
|  | Magnet Eng'r | 24
|  | Elec. Eng'r | 24
|  | Drafter/Designer | 400
| Final Design Review | Fluids Eng'r | 60
|  | Magnet Eng'r | 16
|  | Elec. Eng'r | 16
|  | Drafter/Designer | 100
|  | Machine Eng/Phys | 60
| Installation | Fluids Eng'r | 120
|  | Magnet Eng'r | 20
|  | Elec. Eng'r | 20
|  | Drafter/Designer | 40
| Installation Document Review & As-Builts | Fluids Eng'r | 40
|  | Magnet Eng'r | 4
|  | Elec. Eng'r | 4
|  | Drafter/Designer | 60
PIPE & BUS REMOVAL
Global LCW Pipe:
| Shut down MI LCW system, isolate, drain and prep for long term shutdown | Fluids Tech | 48 |  |  | 3 techs x 2 days
| Disconnect dipoles, quads, remove hoses, flags, move to storage | Fluids Tech | 48 |  |  | 3 techs x 2 days
Quadrupole Bus:
Dipole Bus:
MI-14 LCW & Fluorinert Pipe:
| Shut down MI-14 Fluorinert system, isolate, drain both LCW and Fuorinert sides of system | Fluids Tech | 48 |  |  | 3 techs x 2 days
|  | Kicker Tech | 8 |  |  | 1 tech x 1 day
| Empty MI-14 Girardi box, and penetrations to Q-105 | Fluids Tech | 16 |  |  | 2 days, cubic yards of poly beads to deal with
|  | Rad Tech | 16
|  | Bead Removal Crew | 32
| Task Manager for above | Fluids Tech | 120 |  |  | Full length of construction + prep / wrap up
ENCLOSURE UTILITIES PREP FOR TO REINSTALL
Beneficial occupancy, all survey & layout work complete
PIPE & BUS INSTALLATION
Global LCW Pipe:
| Reinstall all hoses, brackets, any misc. | Fluids Tech | 32 |  |  | 2 techs x 2 days
| Fill & test system headers | Fluids Tech | 16 |  |  | 2 techs x 1 day - DO NOT FILL UNTIL READY! hydrostatic test not required nor advisable
| Bring system to operational status | Fluids Tech | 16 |  |  | 2 techs x 1 day
| Valve in quad cells | Fluids Tech | 8 |  |  | 2 techs x 0.5 days
| Task Manager for above | Fluids Tech | 240 |  |  | 30 DAYS Full length of construction + prep / wrap up
MI-14 Fluorinert & LCW Pipe:
| Inspect & prep penetrations between MI-14 to Q-105 for piping fit | Fluids Eng'r | 8
|  | Drafter/Designer | 8
|  | Task Manager | 12
| Install LCW hoses to header | Fluids Tech | 4
| Fill & test MI-14 skid system | Fluids Tech | 4
| Refill MI-14 Girardi box, and penetrations to Q-105 | Fluids Tech | 8 |  |  | cubic yards of poly beads to deal with
|  | Rad Tech | 8
|  | Bead Refill Crew | 24
z | Reinstall all hoses, brackets, any misc. | Fluids Tech | 8
| Fill & test system headers, Valve in kickers | Fluids Tech | 8 |  |  | NOT UNTIL READY! hydrostatic test not required nor a good idea
|  | Kicker Tech | 8
| Task Manager for above | Fluids Tech | 120 |  |  | Full length of construction + prep / wrap up
| Primary Beamline LCW Fill Line Pipe: |  |  |  |  | New line, no removal necessary
| Install all hoses, brackets, any misc. | Fluids Tech | 8
| Fill & test system line | Fluids Tech | 4 |  |  | NOT UNTIL READY! hydrostatic test not required nor a good idea
| Task Manager for above | Fluids Tech | 24 |  |  | Full length of construction + prep / wrap up
Quadrupole Bus:
| On-site fab & braze of 7/8" bus connection x 2 at each quad | Fluids Tech | 32 |  |  | Often lab insisted to be Fermi techs for magnet connections
| Task Manager for above | Fluids Tech | 96 |  |  | Full length of construction + prep / wrap up
| Dipole Bus: |  |  |  |  | min 6 man crew, Q-103 thru Q-107, 15 lbs/ft, 5 pair in sets @ ~ 600 lbs/set; requires sync w/ magnet installation
| Retrieve dipole bus, flags, brackets, etc from storage and/or delivery | Fluids Tech | 8 |  |  | 2 techs x .5 day
| Reinstall & certify flags | Elec. Tech | 16 |  |  | 2 techs x 2 days
| Reinstall hoses | Fluids Tech | 16
| Task Manager for above | Fluids Tech | 40 |  |  | Full length of construction + prep / wrap up
REFER TO C. GATTUSO ESTIMATE,
BOE Report 131.NSCFB.03.05.05_Installation Coordination

## Mat'ls - New 12-1-22
LBNF EXTRACTION LINE
MI-10 Q-103 thru Q-107 LCW & BUS RETROFIT
LABOR ESTIMATE - NEW - PRELIMINARY DESIGN
MI Cells being modified: | Q-103 - step out | 2 |  | btwn D-102-2 & US Q-103 |  |  |  |  | RFQ
| Q-104 | 2 | [6 empty] | Description | Qnt'y | Each | Total
| Q-105 | 2 | [6 empty] | 1" thread-o-let | 18 | 15.29 | 275.22
| Q-106 | 2 | [6 empty] | 1" nipple | 18 | 2.57 | 46.26
| Q-107 - return back | 2 |  | over end of D-107-2, before Q-108 |  |  |  |  | 1" MNPT x 90 elbow | 18 | 5.12 | 92.16
MI-14 taps | DS end of Q-105 | 2
LBNF PB fill line, new | D-106-2 | 1 | [6 empty] | 2" Sch 10 | 200 | 12.91 | 2582
|  | 13 | [6 empty] | 2" x 45 elbow | 16 | 7.39 | 118.24
[9 empty] | 2" x 90 elbow | 30 | 7.38 | 221.4
[9 empty] | 6" sch10 SS | 500 | 36.69 | 18345
Aisle cross-over extensions |  |  |  | ceiling run= 2" x 10' | 130 | 12.91 | 1678.3 |  | 6 x 6 x 2 Tee | 13 | 183.98 | 2391.74
|  |  |  | wall run = 2" x 4' | 52 | 12.91 | 671.32 |  | 6" x 45 elbow | 2 | 44.47 | 88.94
|  |  |  | 2" x 90 elbow | 16 | 7.38 | 118.08 |  | 6" x 90 elbow | 2 | 63.83 | 127.66
|  |  |  | 2" x 45 elbow | 16 | 7.39 | 118.24
|  |  |  | 2" ball valve | 1 | 300 | 300 |  | 3" Sch 10 | 200 | 20.57 | 4114
[7 empty] | 2885.94 |  | 3" x 45 elbow | 20 | 12.85 | 257
[9 empty] | 3" x 90 elbow | 20 | 14.99 | 299.8
Component taps, to mfld's or header | 9 each S and R | 18 |  | 1" thread-o-let | 18 | 15.29 | 275.22 |  | 6 x 6 x 3 Tee | 20 | 149.1 | 2982
|  |  |  | 1" nipple | 18 | 2.57 | 46.26 |  | 6" cap | 4 | 26.4 | 105.6
|  |  |  | 1" ball valve | 18 | 140 | 2520
|  |  |  | 1" MNPT x 90 elbow | 18 | 5.12 | 92.16 |  | 1" ball valve | 18 | 142.5 | 2565
[7 empty] | 2933.64 |  | 2" ball valve | 13 | 308.34 | 4008.42
Pipe organ Corssover at Q-107 |  |  |  | 3" Sch 10 | 200 | 20.57 | 4114
|  |  |  | 3" x 45 elbow | 20 | 12.85 | 257
|  |  |  | 3" x 90 elbow | 20 | 14.99 | 299.8
|  |  |  | 6 x 6 x 3 Tee | 20 | 149.1 | 2982
|  |  |  | 6" cap | 4 | 26.4 | 105.6
7758.4
6" Header, US End Mods |  |  |  | 6" sch10 SS | 20 | 36.69 | 733.8
|  |  |  | 6" x 90 elbow | 2 | 63.83 | 127.66
|  |  |  | 6" x 45 elbow | 4 | 44.47 | 177.88
1039.34
Hardware |  |  |  | LCW Wall Brackets | 37 | 185 | 6845 | $185 each for PB LCW 2018, spaced at 7', + 2
|  |  |  | Hoses | 26 | 250 | 6500 | Est.
|  |  |  | Manifold Wall Brackets | 39 | 75 | 2925 | Est.
|  |  |  | Bus Wall Brackets | 37 | 25 | 925 | Est.
|  |  |  | Hardware etc, lot | 1 | 2000 | 2000 | Est.
19195
Buswork |  |  |  | Bus Wall Brackets | 37 | 125 | 4625 | Est.
|  |  |  | Bracket Hardware, lot | 1 | 500 | 500 | Est.
|  |  |  | Flag Hardware, lot | 1 | 200 | 200 | Est.
|  |  |  | Insulators | 0 | 0 | 0 | Re-use + stock on hand
|  |  |  | Hoses | 1 | 2000 | 2000 | Est.
|  |  |  | 2-1/8" Make-up Bus | 0 | 0 | 0 | Use existing TeV 2" square bus
|  |  |  | 7/8 x 5/8 x 48" Bus | 10 | 35 | 350 | 5 lb @ $7/lb
|  |  |  | Brazing Consumables, lot | 1 | 1000 | 1000 | Est.
8675
6" Header, full replacement risk |  |  | Header | 6" sch10 SS | 500 | 36.69 | 18345
250' approx length of affected header, R & S |  |  |  | 6" x 90 elbow | 4 | 63.83 | 255.32
|  |  |  | 6" x 45 elbow | 2 | 44.47 | 88.94
|  |  | Taps x 13 | 6 x 6 x 2 Tee | 13 | 183.98 | 2391.74
|  |  |  | 2" x 90 elbow | 13 | 7.38 | 95.94
|  |  |  | 2" ball valve | 13 | 300 | 3900
25076.94
SUMMARY
Aisle cross-over extensions | 2885.94
Component taps, to mfld's or header | 2933.64
Pipe organ Corssover at Q-107 | 7758.4
6" Header, US End Mods | 1039.34
Hardware | 19195
Buswork | 8675
42487.32
6" Header, full replacement risk | 25076.94

## Mat'ls - Quotes
MI Cells being modified: | Q-103 - step out | 2 |  | btwn D-102-2 & US Q-103
| Q-104 | 2
| Q-105 | 2
| Q-106 | 2 | [5 empty] | RFQ
| Q-107 - return back | 2 |  | over end of D-107-2, before Q-108 |  |  |  | Description | Qnt'y | Each | Total
MI-14 taps | DS end of Q-105 | 2 |  |  | 130 | 12.91 | 1678.3 | 1" thread-o-let | 18 | 15.29 | 275.22
LBNF PB fill line, new | D-106-2 | 1 |  |  | 52 | 12.91 | 671.32 | 1" nipple | 18 | 2.57 | 46.26
Aisle cross-over extensions, ttl req'd |  | 13 |  |  | 16 | 7.38 | 118.08 | 1" MNPT x 90 elbow | 18 | 5.12 | 92.16
[5 empty] | 16 | 7.39 | 118.24
Aisle cross-over extensions |  |  |  | ceiling run= 2" x 10' | 1 | 300 | 300 | 2" Sch 10 | 200 | 12.91 | 2582
|  |  |  | wall run = 2" x 4' |  |  |  | 2" x 45 elbow | 16 | 7.39 | 118.24
|  |  |  | 2" x 90 elbow | 18 | 15.29 | 275.22 | 2" x 90 elbow | 30 | 7.38 | 221.4
|  |  |  | 2" x 45 elbow | 18 | 2.57 | 46.26
|  |  |  | 2" ball valve | 18 | 140 | 2520 | 6" sch10 SS | 500 | 36.69 | 18345
[5 empty] | 18 | 5.12 | 92.16 | 6 x 6 x 2 Tee | 13 | 183.98 | 2391.74
Component taps, to mfld's or header | 9 each S and R | 18 |  | 1" thread-o-let |  |  |  | 6" x 45 elbow | 2 | 44.47 | 88.94
|  |  |  | 1" nipple |  |  |  | 6" x 90 elbow | 2 | 63.83 | 127.66
|  |  |  | 1" ball valve | 200 | 20.57 | 4114
|  |  |  | 1" MNPT x 90 elbow | 20 | 12.85 | 257 | 3" Sch 10 | 200 | 20.57 | 4114
[5 empty] | 20 | 14.99 | 299.8 | 3" x 45 elbow | 20 | 12.85 | 257
[5 empty] | 20 | 149.1 | 2982 | 3" x 90 elbow | 20 | 14.99 | 299.8
Pipe Organ Crossover at Q-107 |  |  |  | 3" Sch 10 | 4 | 26.4 | 105.6 | 6 x 6 x 3 Tee | 20 | 149.1 | 2982
|  |  |  | 3" x 45 elbow |  |  |  | 6" cap | 4 | 26.4 | 105.6
3" x 90 elbow
|  |  |  | 6 x 6 x 3 Tee | 20 | 36.69 | 733.8 | 1" ball valve | 18 | 142.5 | 2565
|  |  |  | 6" cap | 2 | 63.83 | 127.66 | 2" ball valve | 13 | 308.34 | 4008.42
[5 empty] | 4 | 44.47 | 177.88
6" Header, US End Mods |  |  |  | 6" sch10 SS
6" x 90 elbow
6" x 45 elbow
[5 empty] | 500 | 36.69 | 18345
[5 empty] | 4 | 63.83 | 255.32
[5 empty] | 2 | 44.47 | 88.94
6" Header, full replacement risk |  |  |  |  | 13 | 183.98 | 2391.74
250' approx length of affected header, R & S |  |  | Header | 6" sch10 SS | 13 | 7.38 | 95.94
|  |  |  | 6" x 90 elbow | 13 | 300 | 3900
6" x 45 elbow
|  |  | Taps x 13 | 6 x 6 x 2 Tee
2" x 90 elbow
2" ball valve
688.82/gal
742.80/gal
965.26/gal

## Mat'ls - old
LBNF EXTRACTION LINE
MI-10 Q-103 thru Q-107 LCW & BUS RETROFIT
LABOR ESTIMATE - OLD
Pre-2019 |  |  |  |  | 2022 Update
Materials | 30000 | 30000
6" pipe | on hand ? | 500 | guess |  | 40' to make up 6" ends/transitions, if necessary
2" manifold, pipe | on hand ? | 500 | guess |  | 4 quads x 10' x 2 = 160'
Hdr crossover, 3" pipe |  |  |  |  | 2 runs x 5 pipes each x 10'/pipe =100'
Hdr crossover, 3" 45 elbow |  |  |  |  | 2 runs x 5 pipes each x 1/pipe = 10
Hdr crossover, 3" 90 elbow |  |  |  |  | 2 runs x 5 pipes each x 2/pipe = 20
Hdr crossover, 6" x 3" tee |  |  |  |  | 2 runs x 5 pipes each x 2/pipe = 20 | could use T-drill ends
Hdr crossover, 6" pipe cap |  |  |  |  | 2 runs x 2 each = 4
Mfld extension, 2" pipe |  |  |  |  | 2 runs x 5 pipes each x 14'/pipe =140'
Mfld extension, 2" 90 elbow |  |  |  |  | 2 runs x 5 pipes each x 2/pipe = 20
Misc Fittings |  | 1000 | guess
LCW brackets @ 7' + 2 | 240'/7' = 35, + 2 = 37 | 7400 | 37 * 200 = 7400 | $185 each for PB LCW 2018
Hardware, Clamps, etc |  | 500 | guess
Hoses |  | 1000 | guess |  | re-use but replace w/ new
Bus, 1"x4" or 2-5/8"D |  | 6000 | guess | $90/ft for quantity | Re-use
Bus, 2-1/8"D |  | 4000 | guess | $50/ft for quantity | As needed for mods, re-routing, flags, 100', use 2" sq Tevatron bus
Bus Flags |  | 6000 | guess |  | dipoles - 10 pair - what can we re-use?
Bus candy canes |  |  |  |  | 5 quadrupoles, 2 each x 5' = 50', 7/8OD x 1/8W
Hardware, Clamps, etc |  | 1000 | guess
Hoses |  | 2000 | guess |  | re-use but replace w/ new
29900
this hasn't been updated in ages

## Beamline
LBNF MI-10 Area LCW and Bus Retrofit for Extraction Beamline
MI Cells actually being modified:
| Q-103 - step out @ alcove wall |  |  | btwn D-102-2 & US Q-103
Q-104
Q-105
Q-106
| Q-107 - return back in |  |  | over end of D-107-2, before Q-108
quad count = 5
dipole count = 10
[17 empty] | MI-10 | MI-10 |  |  | Extraction
All work assumes isolation and draining of all LCW and bus through this sector | [16 empty] | Alcove | Alcove |  |  | Beamline
[17 empty] | West | East |  |  | Start
[17 empty] | Wall | Wall
EXISTING MAIN INJECTOR BEAMLINE
| Q - 108 | D - 107 - 2 | D - 107 | Q - 107 | D - 106 - 2 | D - 106 | Q - 106 | D - 105 - 2 | D - 105 | Q - 105 | D - 104 - 2 | D - 104 | Q - 104 | D - 103 - 2 | D - 103 | Q - 103 | kicker | kicker | Q - 102 |  |  | Q - 101 |  | Q - 100
MI-14 LCW-Fluorinert
2" for PBL fill
dipole "quad bypass" bus temp removal
quad bus relocate
LCW relocate
| ADDITIONAL EXTRACTION BEAMLINE | [5 empty] | beamline penetration
[11 empty] | Q-204 | Q-203 | H-202 | Q-202 | Q-201 | V-100 | LAM-11B | LAM-11A | (Q-102) | LAM-10
|  |  | ` | [7 empty] | 3Q120 | 3Q120 | D | 3Q60 | 3Q60 | C-magnet | Lambertson | Lambertson |  | Lambertson
extraction beamline added
[17 empty] | MI-10 | MI-10
[17 empty] | Alcove | Alcove
[17 empty] | West | East
[17 empty] | Wall | Wall
| Modified Existing MI Piping & Bus | [14 empty] | Added Extraction Line Magnets
|  |  |  | LCW Piping | [12 empty] | PB Extraction Line
|  |  |  | Disconnect / Remove |  |  | Modify / Move |  |  | Install / Reconnect | [6 empty] | LCW to magnets only, no add'l buswork
|  |  |  | hoses | 6" header | 2" manifold** | 6" header | 2" manifold | hoses | 6" header | 2" manifold | hoses | ** may be partial removal for mods |  |  | # | Component | LCW Doner? | Flow | MI Quad Tap | Add'l per quad
| Q-103 - step out @ alcove wall |  |  | X | x-over | X | x-over | X |  | x-over | X | X |  |  |  | 1 | LAM-10 | Q-102 | 16
| Q-104 |  |  | X | X | X | aisle | X |  | all | X | X |  |  |  | 2 | LAM-11A | Q-102 | 16
| Q-105 |  |  | X | X | X | aisle | X |  | all | X | X |  |  |  | 3 | LAM-11B | Q-102 or 103 | 16 | Q-102 | 48
| Q-106 |  |  | X | X | X | aisle | X |  | all | X | X |  |  |  | 4 | V-100 | Q-102 or 103 | 9
| Q-107 - return back in |  |  | X | x-over | X | x-over | X |  | x-over | X | X |  |  |  | 5 | Q-201A | Q-103 | 8
[16 empty] | 6 | Q-201B | Q-103 | 8
[16 empty] | 7 | HV-201 | Q-103 | 9
[16 empty] | 8 | Q-202 | Q-104 | 8 | Q-103 | 25
|  |  |  | DIPOLE | [11 empty] | 9 | Q-203 | Q-104 | 6 | Q-104 | 6
|  |  |  | Disconnect / Remove |  |  | Modify / Move |  |  | Install / Reconnect
|  |  |  | flag | hoses | 1"x4" bus | bus | flag | hoses | 1"x4" bus | flag | hoses |  |  |  |  | full line |  | 96
| Q-103 - step out @ alcove wall |  |  | X | X | X | maybe | maybe | maybe | X | X | X |  |  |  |  | additional LCW reqmts, gpm |  |  |  | 100 ?
| Q-104 |  |  | X | X | X | no | no | no | X | X | X
| Q-105 |  |  | X | X | X | no | no | no | X | X | X
| Q-106 |  |  | X | X | X | no | no | no | X | X | X
| Q-107 - return back in |  |  | X | X | X | no | no | no | X | X | X
MAIN INJECTOR - SCHEMATIC FLOWS
|  |  |  | QUADRUPOLE | [11 empty] | Full MI-RR-Extraction Line Magnets |  |  |  |  | * LCW change to magnets only, buswork no change |  |  |  | Q-639 thru Q-108 |  |  |  |  | comp flow ttl in yellow do not agree w tap flow ttl
|  |  |  | Disconnect / Remove |  |  | Modify / Move |  |  | Install / Reconnect | [6 empty] | Ref ME-305689 | [7 empty] | ME-305689 |  |  |  |  | remove for extraction line
|  |  |  | 7/8" bus / elec + LCW |  | 2-1/8" bus | 7/8" bus / elec + LCW |  | 2-1/8" bus* | 2-1/8" bus* | 7/8" bus / elec + LCW |  | * may use TeV 2" square bus |  |  | NEEDS CHECKED | [8 empty] | SUPPLY - current |  |  |  |  | RETURN - current
| Q-103 - step out @ alcove wall |  |  | X |  |  | X |  | X | X | X | [7 empty] | Compnt Flow | Source | Old Flow | Change | New Flow |  |  |  | component | station | dwg |  |  | component |  | station | dwg
| Q-104 |  |  | X |  |  | X |  | X | X | X |  |  |  |  | # | Component | Status | gpm |  | gpm | gpm | gpm |  | station | component | flow | sum | shown | station | component | flow | subttls | sum | shown
| Q-105 |  |  | X |  |  | X |  | X | X | X | [5 empty] | SQA-851 | gone | -10 | Q-641 |  |  |  |  | Q-639 | D-638-2 | 8 |  |  | Q-639 | D-638-2 | 4 + 4 | 8
| Q-106 |  |  | X |  |  | X |  | X | X | X | [5 empty] | D-640-2 | [8 empty] | Q-639 | 12 |  |  |  | D-639-1 | 4 + 4 | 8 | 16
| Q-107 - return back in |  |  | X |  |  | X |  | X | X | X | [5 empty] | Q-8511 | [8 empty] | Q-641 | 12
[17 empty] | D-641-1 | [8 empty] | D-639-1 | 8 | 40
[25 empty] | Q-640 | D-639-2 | 8 |  |  | Q-640 | D-639-2 | 4 + 4 | 8
[17 empty] | D-641-2 | stay | 8 | Q-100 | [5 empty] | Q-640 | 12 |  |  |  | D-640-1 | 4 + 4 | 8 | 16
[16 empty] | 0 | Q-100 | stay | 12 | Q-100 | [5 empty] | Q-100 | 12
[17 empty] | SQA-852 | gone | -10 | Q-100 | [5 empty] | D-640-1 | 8 | 40
[17 empty] | A-0 LAMB | gone | -10 | Q-101 |  |  |  |  | Q-641 | D-640-2 | 8 |  |  | Q-641 | SQA-851 | 10 | 10
[17 empty] | Q-101 | stay | 10 | Q-101 | [5 empty] | SQA-851 | 10 |  |  |  | D-640-2 | 4 + 4 | 8
[17 empty] | MLAW-RR | stay | 7 | Q-102 | [5 empty] | Q-8511 | 10 |  |  |  | D-641-1 | 4 + 4 | 8
|  | LBNE Magnet Lattice from 2014-05-06 Dwg F10021519 (Loop/Circuit designations by S. Hays 2015-02-03) | [13 empty] | 1 | LAM-10 | add | 16 | Q-102 | [5 empty] | D-641-1 | 8 | 36 | 16 |  | Q-641 | 12 | 12
|  | Magnet ID | Type | Loop/ Circuit | Elev. Ft. | GPM @ 100 PD | Power kW | LCW TD (dF) | Notes All magnet flows rounded up to the next 1 GPM | [7 empty] | Q-102 | stay | 10 | Q-102 | [10 empty] | Q-101 | 10 | 10
| 1 | LAM10 | ILA - Lambertson | E:LAM1 | 715.7 | 16 | 8.259 | 3.5235 | GPM per magnet label | [6 empty] | 2 | LAM-11A | add | 16 | Q-102 | [10 empty] | Q-8511 | 10? | 10 | 58 | 38
|  | Q102 | 3Q84 |  | 715.7 |  |  |  | Existing - fed from MI Magnet LCW system | [6 empty] | 3 | LAM-11B | add | 16 | Q-102 |  |  |  |  | Q-100 | D-641-2 | 8 |  |  | Q-100 | Q-100 | 12 | 12
| 2 | LAM11A | ILA - Lambertson | E:LAM12 | 715.75 | 16 | 32.351 | 13.8016 | GPM per magnet label | [7 empty] | Stoich Tank | gone | -5 | Header | [5 empty] | SQA-852 | 10 | 18 |  |  | Q-102 | 10 | 10
| 3 | LAM11B | ILA - Lambertson | E:LAM12 | 715.8 | 16 | 32.351 | 13.8016 | GPM per magnet label | [7 empty] | KICK | gone | -2 | Q-103 | [10 empty] | SQA-852 | 10 | 10 | 32 | 48
| 4 | V100 | ICA Trim | E:V1001 | 716 | 9 | 16.597 | 12.5878 | [8 empty] | KICK | gone | -2 | Q-103 |  |  |  |  | Q-101 | LAMB AZERO | 10 |  |  | Q-101 | LAMB AZERO | 10 | 10 | 10
| 5 | Q201A | QQU - 3Q60 Quad | E:Q201 | 716.5 | 8 | 1.2845 | 1.096 | [7 empty] | 4 | V-100 | add | 9 | Q-103 | [5 empty] | Q-101 | 10
| 6 | Q201B | QQU - 3Q60 Quad | E:Q201 | 716.8 | 8 | 1.2845 | 1.096 | [7 empty] | 5 | Q-201A | add | 8 | Q-103 | [5 empty] | Q-103 | 10 | 30
| 7 | H202 | IDA Dipole | H:202 | 717.2 | 15 | 24.256 | 11.038 | [8 empty] | Q-103 | stay | 10 | Q-103 |  |  |  |  | Q-102 | MLAW | 7 |  |  | Q-102 | MLAW | 7 | 7 | 7
| 8 | Q202 | QQB - 3Q120 Quad | E:Q203 | 717.6 | 6 | 3.314 | 3.7702 | [7 empty] | 6 | Q-201B | add | 8 | Q-103 | [5 empty] | Q-102 | 10
| 9 | Q203 | QQB - 3Q120 Quad | E:Q204 | 718.1 | 6 | 1.956 | 2.2253 | [7 empty] | 7 | HV-201 | add | 9 | Q-103 | [5 empty] | Q-104 | 12 | 29 | 22
[17 empty] | Stoich Tank | gone | -5 | Header |  |  |  |  | HDR-102 | STOICH | 5 | 5 |  | HDR-102 | STOICH | 5 | 5 | 5
[16 empty] | 8 | Q-202 | add | 8 | Q-104 |  |  |  |  | Q-103 | Kickers | 4 | 4 |  | Q-103 | Kickers | 2 + 2 | 4
[17 empty] | Q-104 | stay | 12 | Q-104 | [10 empty] | Q-103 | 10 | 10
[17 empty] | D-104-1 | stay | 8 | Q-104 | [10 empty] | Q-105 | 12 | 12 | 26
[17 empty] | D-104-2 | stay | 8 | Q-105 |  |  |  |  | HDR-103 | STOICH | 5 | 5 |  | HDR-103 | STOICH | 5 | 5 | 5
[16 empty] | 9 | Q-203 | add | 6 | Q-105 |  |  |  |  | Q-104 | D-104-1 | 8 | 8 |  | Q-104 | D-641-2 | 4 + 4 | 8
[17 empty] | Q-105 | stay | 12 | Q-105 | [10 empty] | D-104-1 | 4 + 4 | 8
[17 empty] | D-105-1 | stay | 8 | Q-105 | [10 empty] | Q-104 | 12 | 12
[17 empty] | D-105-2 | stay | 8 | Q-106 | [10 empty] | Q-106 | 12 | 12 | 40
[17 empty] | Q-106 | stay | 12 | Q-106 |  |  |  |  | Q-105 | D-104-2 | 8 |  |  | Q-105 | D-104-2 | 4 + 4 | 8
[17 empty] | D-106-1 | stay | 8 | Q-106 | [5 empty] | Q-105 | 12 |  |  |  | D-105-1 | 4 + 4 | 8 | 16
[17 empty] | Stoich Tank | gone | -5 | Header | [5 empty] | Q-107 | 12
[17 empty] | D-106-2 | stay | 8 | Q-107 | [5 empty] | D-105-1 | 8 | 40
[17 empty] | Q-107 | stay | 12 | Q-107 |  |  |  |  | Q-106 | D-105-2 | 8 |  |  | Q-106 | D-105-2 | 4 + 4 | 8
[17 empty] | D-107-1 | stay | 8 | Q-107 | [5 empty] | Q-106 | 12 |  |  |  | D-106-1 | 4 + 4 | 8 | 16
[26 empty] | Q-108 | 12
[26 empty] | D-106-1 | 8 | 40
[25 empty] | HDR-106 | STOICH | 5 | 5 |  | HDR-106 | STOICH | 5 | 5 | 5
[25 empty] | Q-107 | D-106-2 | 8 |  |  | Q-107 | D-106-2 | 4 + 4 | 8
[26 empty] | D-107-1 | 8 | 16 |  |  | D-107-1 | 4 + 4 | 8
[31 empty] | Q-107 | 12 | 12
[31 empty] | Q-109 | 10 | 10 | 38
[25 empty] | Q-108 | D-107-2 | 8 |  |  | Q-108 | D-107-2 | 4 + 4 | 8
[26 empty] | S-108 | 1 |  |  |  | D-108-1 | 4 + 4 | 8
[26 empty] | D-108-1 | 10 | 19 |  |  | Q-108 | 12 | 12
[31 empty] | Q-110 | 10 | 10
[31 empty] | S-108 | 1 | 1 | 39

## 1 - ME-305689 - original Rev D
MAIN INJECTOR - SCHEMATIC FLOWS |  |  |  |  | ALL FLOWS IN GPM
Q-639 thru Q-108 |  |  |  |  | flow ttl in yellow do not agree w dwg ttl
ME-305689 |  |  |  |  | remove for extraction line | [5 empty] | Components to Remove
SUPPLY - current |  | Component | math sum | flow at tap | RETURN - current |  | Component |  | sum at | flow at tap
Location | Component | Flow, gpm | at tap | as shown | Location | Component | Flow, gpm | subttls | tap | as shown | Location | Component | Flow
Q-639 | D-638-2 | 8 |  |  | Q-639 | D-638-2 | 4 + 4 | 8 |  |  | Q-641 | SQA-851 | 10
| Q-639 | 12 |  |  |  | D-639-1 | 4 + 4 | 8 | 16 |  | Q-100 | SQA-852 | 10
| Q-641 | 12 | [8 empty] | Q-101 | LAMB AZERO | 10
| D-639-1 | 8 | 40 | [7 empty] | HDR-102 | STOICH | 5
Q-640 | D-639-2 | 8 |  |  | Q-640 | D-639-2 | 4 + 4 | 8 |  |  | Q-103 | 2 Kickers | 4
| Q-640 | 12 |  |  |  | D-640-1 | 4 + 4 | 8 | 16 |  | HDR-103 | STOICH | 5
| Q-100 | 12 | [8 empty] | HDR-106 | STOICH | 5
| D-640-1 | 8 | 40
Q-641 | D-640-2 | 8 |  |  | Q-641 | SQA-851 | 10 | 10 |  |  | Reduced Flow, ttl |  | 49
| SQA-851 | 10 |  |  |  | D-640-2 | 4 + 4 | 8
| Q-8511 | 10 |  |  |  | D-641-1 | 4 + 4 | 8
| D-641-1 | 8 | 36 | 16 |  | Q-641 | 12 | 12
[6 empty] | Q-101 | 10 | 10
[6 empty] | Q-8511 | 10? | 10 | 58 | 38
Q-100 | D-641-2 | 8 |  |  | Q-100 | Q-100 | 12 | 12
| SQA-852 | 10 | 18 |  |  | Q-102 | 10 | 10
[6 empty] | SQA-852 | 10 | 10 | 32 | 48
Q-101 | LAMB AZERO | 10 |  |  | Q-101 | LAMB AZERO | 10 | 10 | 10
| Q-101 | 10
| Q-103 | 10 | 30
Q-102 | MLAW | 7 |  |  | Q-102 | MLAW | 7 | 7 | 7
| Q-102 | 10
| Q-104 | 12 | 29 | 22
HDR-102 | STOICH | 5 | 5 |  | HDR-102 | STOICH | 5 | 5 | 5
Q-103 | Kickers | 4 | 4 |  | Q-103 | Kickers | 2 + 2 | 4
[6 empty] | Q-103 | 10 | 10
[6 empty] | Q-105 | 12 | 12 | 26
HDR-103 | STOICH | 5 | 5 |  | HDR-103 | STOICH | 5 | 5 | 5
Q-104 | D-104-1 | 8 | 8 |  | Q-104 | D-641-2 | 4 + 4 | 8
[6 empty] | D-104-1 | 4 + 4 | 8
[6 empty] | Q-104 | 12 | 12
[6 empty] | Q-106 | 12 | 12 | 40
Q-105 | D-104-2 | 8 |  |  | Q-105 | D-104-2 | 4 + 4 | 8
| Q-105 | 12 |  |  |  | D-105-1 | 4 + 4 | 8 | 16
| Q-107 | 12
| D-105-1 | 8 | 40
Q-106 | D-105-2 | 8 |  |  | Q-106 | D-105-2 | 4 + 4 | 8
| Q-106 | 12 |  |  |  | D-106-1 | 4 + 4 | 8 | 16
| Q-108 | 12
| D-106-1 | 8 | 40
HDR-106 | STOICH | 5 | 5 |  | HDR-106 | STOICH | 5 | 5 | 5
Q-107 | D-106-2 | 8 |  |  | Q-107 | D-106-2 | 4 + 4 | 8
| D-107-1 | 8 | 16 |  |  | D-107-1 | 4 + 4 | 8
[6 empty] | Q-107 | 12 | 12
[6 empty] | Q-109 | 10 | 10 | 38
Q-108 | D-107-2 | 8 |  |  | Q-108 | D-107-2 | 4 + 4 | 8
| S-108 | 1 |  |  |  | D-108-1 | 4 + 4 | 8
| D-108-1 | 10 | 19 |  |  | Q-108 | 12 | 12
[6 empty] | Q-110 | 10 | 10
[6 empty] | S-108 | 1 | 1 | 39

## 2 - ME-305689 - corrected Rev E
MAIN INJECTOR - SCHEMATIC FLOWS |  |  |  | ALL FLOWS IN GPM
Q-639 thru Q-108
ME-305689 |  |  |  | remove for extraction line
SUPPLY - current |  |  | correct sum | RETURN - current |  |  |  | correct sum
Location | Component | subttls | at tap | Location | Component |  | subttls | at tap
Q-639 | D-638-2 | 8 |  | Q-639 | D-638-2 | 4 + 4 | 8
| Q-639 | 12 |  |  | D-639-1 | 4 + 4 | 8 | 16
| Q-641 | 12
| D-639-1 | 8 | 40
Q-640 | D-639-2 | 8 |  | Q-640 | D-639-2 | 4 + 4 | 8
| Q-640 | 12 |  |  | D-640-1 | 4 + 4 | 8 | 16 | `
| Q-100 | 12
| D-640-1 | 8 | 40
Q-641 | D-640-2 | 8 |  | Q-641 | SQA-851 | 10 | 10
| SQA-851 | 10 |  |  | D-640-2 | 4 + 4 | 8
| Q-8511 | 10 |  |  | D-641-1 | 4 + 4 | 8
| D-641-1 | 8 | 36 |  | Q-641 | 12 | 12
[5 empty] | Q-101 | 10 | 10
[5 empty] | Q-8511 | 10? | 10 | 58
Q-100 | D-641-2 | 8 |  | Q-100 | Q-100 | 12 | 12
| SQA-852 | 10 | 18 |  | Q-102 | 10 | 10
[5 empty] | SQA-852 | 10 | 10 | 32
Q-101 | LAMB AZERO | 10 |  | Q-101 | LAMB AZERO | 10 | 10 | 10
| Q-101 | 10
| Q-103 | 10 | 30
Q-102 | MLAW | 7 |  | Q-102 | MLAW | 7 | 7 | 7
| Q-102 | 10
| Q-104 | 12 | 29
HDR-102 | STOICH | 5 | 5 | HDR-102 | STOICH | 5 | 5 | 5
Q-103 | Kickers | 4 | 4 | Q-103 | Kickers | 2 + 2 | 4
[5 empty] | Q-103 | 10 | 10
[5 empty] | Q-105 | 12 | 12 | 26
HDR-103 | STOICH | 5 | 5 | HDR-103 | STOICH | 5 | 5 | 5
Q-104 | D-104-1 | 8 | 8 | Q-104 | D-641-2 | 4 + 4 | 8
[5 empty] | D-104-1 | 4 + 4 | 8
[5 empty] | Q-104 | 12 | 12
[5 empty] | Q-106 | 12 | 12 | 40
Q-105 | D-104-2 | 8 |  | Q-105 | D-104-2 | 4 + 4 | 8
| Q-105 | 12 |  |  | D-105-1 | 4 + 4 | 8 | 16
| Q-107 | 12
| D-105-1 | 8 | 40
Q-106 | D-105-2 | 8 |  | Q-106 | D-105-2 | 4 + 4 | 8
| Q-106 | 12 |  |  | D-106-1 | 4 + 4 | 8 | 16
| Q-108 | 12
| D-106-1 | 8 | 40
HDR-106 | STOICH | 5 | 5 | HDR-106 | STOICH | 5 | 5 | 5
Q-107 | D-106-2 | 8 |  | Q-107 | D-106-2 | 4 + 4 | 8
| D-107-1 | 8 | 16 |  | D-107-1 | 4 + 4 | 8
[5 empty] | Q-107 | 12 | 12
[5 empty] | Q-109 | 10 | 10 | 38
Q-108 | D-107-2 | 8 |  | Q-108 | D-107-2 | 4 + 4 | 8
| S-108 | 1 |  |  | D-108-1 | 4 + 4 | 8
| D-108-1 | 10 | 19 |  | Q-108 | 12 | 12
[5 empty] | Q-110 | 10 | 10
[5 empty] | S-108 | 1 | 1 | 39

## 3 - ME-305689 - loads out Rev F
MAIN INJECTOR - SCHEMATIC FLOWS - MANIFOLDS |  |  |  | ALL FLOWS IN GPM |  |  |  | Components to Remove
Q-639 thru Q-108 | [11 empty] | Change per
ME-305689 |  |  |  | remove for extraction line |  |  |  | # | Location | Component | Flow | Location
SUPPLY - current |  |  | correct sum | RETURN - current |  |  | correct sum | 1 | Q-641 | SQA-851 | 10 | -10
Location | Component | subttls | at tap | Location | Component | subttls | at tap | 2 | Q-100 | SQA-852 | 10 | -10
Q-639 | D-638-2 | 8 |  | Q-639 | D-638-2 | 8 |  | 3 | Q-101 | LAMB AZERO | 10 | -10
| Q-639 | 12 |  |  | D-639-1 | 8 | 16 | 4 | HDR-102 | STOICH | 5 | -5
| Q-641 | 12 | [5 empty] | 5 | Q-103 | Kicker 1 | 2
| D-639-1 | 8 | 40 |  |  |  |  | 6 |  | Kicker 2 | 2 | -4
Q-640 | D-639-2 | 8 |  | Q-640 | D-639-2 | 8 |  | 7 | HDR-103 | STOICH | 5 | -5
| Q-640 | 12 |  |  | D-640-1 | 8 | 16 | 8 | HDR-106 | STOICH | 5 | -5
| Q-100 | 12
| D-640-1 | 8 | 40 | [5 empty] | Reduced Flow, ttl |  | 49
Q-641 | D-640-2 | 8 |  | Q-641 | SQA-851 | 0
| SQA-851 | 0 |  |  | D-640-2 | 8
| Q-8511 | 10 |  |  | D-641-1 | 8
| D-641-1 | 8 | 26 |  | Q-641 | 12
[5 empty] | Q-101 | 10
[5 empty] | Q-8511 | 10 | 48
Q-100 | D-641-2 | 8 |  | Q-100 | Q-100 | 12
| SQA-852 | 0 | 8 |  | Q-102 | 10
[5 empty] | SQA-852 | 0 | 22
Q-101 | LAMB AZERO | 0 |  | Q-101 | LAMB AZERO | 0 | 0
| Q-101 | 10
| Q-103 | 10 | 20
Q-102 | MLAW | 7 |  | Q-102 | MLAW | 7 | 7
| Q-102 | 10
| Q-104 | 12 | 29
HDR-102 | STOICH | 0 | 0 | HDR-102 | STOICH | 0 | 0
Q-103 | Kickers | 0 | 0 | Q-103 | Kickers | 0
[5 empty] | Q-103 | 10
[5 empty] | Q-105 | 12 | 22
HDR-103 | STOICH | 0 | 0 | HDR-103 | STOICH | 0 | 0
Q-104 | D-104-1 | 8 | 8 | Q-104 | D-641-2 | 8
[5 empty] | D-104-1 | 8
[5 empty] | Q-104 | 12
[5 empty] | Q-106 | 12 | 40
Q-105 | D-104-2 | 8 |  | Q-105 | D-104-2 | 8
| Q-105 | 12 |  |  | D-105-1 | 8 | 16
| Q-107 | 12
| D-105-1 | 8 | 40
Q-106 | D-105-2 | 8 |  | Q-106 | D-105-2 | 8
| Q-106 | 12 |  |  | D-106-1 | 8 | 16
| Q-108 | 12
| D-106-1 | 8 | 40
HDR-106 | STOICH | 0 | 0 | HDR-106 | STOICH | 0 | 0
Q-107 | D-106-2 | 8 |  | Q-107 | D-106-2 | 8
| D-107-1 | 8 | 16 |  | D-107-1 | 8
[5 empty] | Q-107 | 12
[5 empty] | Q-109 | 10 | 38
Q-108 | D-107-2 | 8 |  | Q-108 | D-107-2 | 8
| S-108 | 1 |  |  | D-108-1 | 8
| D-108-1 | 10 | 19 |  | Q-108 | 12
[5 empty] | Q-110 | 10
[5 empty] | S-108 | 1 | 39

## 4 - ME-305689 - LBNF in Rev G
MAIN INJECTOR - SCHEMATIC FLOWS |  |  |  | ALL FLOWS IN GPM |  |  |  |  | Components to Add |  |  |  |  | Full MI/RR LCW Change in Flow
Q-639 thru Q-108 | [9 empty] | LCW |  |  | Add'l per |  | Flow
ME-305689 |  |  |  | remove for extraction line |  |  |  |  | # | Location* | Component | Flow | Location | Cause | Change, gpm
SUPPLY - current |  |  | correct sum | RETURN - current |  |  | correct sum |  | 1 | Q-102 | LAM-10 | 16 |  | MI Flow reduction | -49
Location | Component | subttls | at tap | Location | Component | subttls | at tap |  | 2 | Q-102 | LAM-11A | 16 |  | LBNF Ext Line Flow Added | 96
Q-639 | D-638-2 | 8 |  | Q-639 | D-638-2 | 8 |  |  | 3 | Q-102 | LAM-11B | 16 | 48
| Q-639 | 12 |  |  | D-639-1 | 8 |  |  | 4 | Q-103 | V-100 | 9 |  | Ttl Change in Flow, MI Q-100 Region | 47
| Q-641 | 12 | [6 empty] | 5 | Q-103 | Q-201A | 8
| D-639-1 | 8 | 40 |  |  |  | 16 |  | 6 | Q-103 | Q-201B | 8 |  | ALSO need to add a 2" fill line to PB LCW about Q-105, DS of MI-14 taps
Q-640 | D-639-2 | 8 |  | Q-640 | D-639-2 | 8 |  |  | 7 | Q-103 | HV-201 | 9 | 34
| Q-640 | 12 |  |  | D-640-1 | 8 |  | ` | 8 | Q-104 | Q-202 | 8
| Q-100 | 12 | [6 empty] | 9 | Q-104 | Q-203 | 6 | 14
| D-640-1 | 8 | 40 |  |  |  | 16
Q-641 | D-640-2 | 8 |  | Q-641 | D-640-2 | 8 |  |  |  | full line add |  | 96
| Q-8511 | 10 |  |  | D-641-1 | 8
| D-641-1 | 8 |  |  | Q-641 | 12
[5 empty] | Q-101 | 10 |  |  | * LCW cells are numbered as centered on the quad, and include 1 dipole US and 1 DS
|  |  | 26 |  | Q-8511 | 10 | 48 |  | LCW increase is to magnets only, no add'l buswork
Q-100 | D-641-2 | 8 |  | Q-100 | Q-100 | 12 |  |  | Manifolds: 2" IPS Sch 10, limit 80 to 100 gpm
|  |  | 8 |  | Q-102 | 10 | 22
Q-101 | Q-101 | 10 |  | Q-101
| Q-103 | 10 | 20 |  |  |  | 0
Q-102 | MLAW | 7 |  | Q-102 | MLAW | 7
| Q-102 | 10 |  |  | LAM-10 | 16
| Q-104 | 12 |  |  | LAM-11A | 16
| LAM-10 | 16 |  |  | LAM-11B | 16
| LAM-11A | 16
| LAM-11B | 16 | 77 |  |  |  | 55
Q-103 | V-100 | 9 |  | Q-103 | Q-103 | 10
| Q-201A | 8 |  |  | Q-105 | 12
| Q-201B | 8 |  |  | V-100 | 9
| HV-201 | 9 |  |  | Q-201A | 8
[5 empty] | Q-201B | 8
|  |  | 34 |  | HV-201 | 9 | 56
Q-104 | D-104-1 | 8 |  | Q-104 | D-641-2 | 8
| Q-202 | 8 |  |  | D-104-1 | 8
| Q-203 | 6 |  |  | Q-104 | 12
[5 empty] | Q-106 | 12
[5 empty] | Q-202 | 8
|  |  | 22 |  | Q-203 | 6 | 54
Q-105 | D-104-2 | 8 |  | Q-105 | D-104-2 | 8
| Q-105 | 12 |  |  | D-105-1 | 8
| Q-107 | 12
| D-105-1 | 8 | 40 |  |  |  | 16
Q-106 | D-105-2 | 8 |  | Q-106 | D-105-2 | 8
| Q-106 | 12 |  |  | D-106-1 | 8
| Q-108 | 12
| D-106-1 | 8 | 40 |  |  |  | 16
Q-107 | D-106-2 | 8 |  | Q-107 | D-106-2 | 8
| D-107-1 | 8 |  |  | D-107-1 | 8
[5 empty] | Q-107 | 12
|  |  | 16 |  | Q-109 | 10 | 38
Q-108 | D-107-2 | 8 |  | Q-108 | D-107-2 | 8
| S-108 | 1 |  |  | D-108-1 | 8
| D-108-1 | 10 |  |  | Q-108 | 12
[5 empty] | Q-110 | 10
|  |  | 19 |  | S-108 | 1 | 39

## AECOM S-EE-102
REMOVAL OF GERARDI BOXES MANDATE REMOVAL OF MI-14 LCW & FLUORINERT LINES
2" IPS SS LCW FILL LINE TO BE LOCATED THRU ONE OF THESE PENETRATIONS

## AECOM S-EE-104
2" IPS SS LCW FILL LINE TO BE LOCATED THRU ONE OF THESE PENETRATIONS
REMOVAL OF GERARDI BOXES MANDATE REMOVAL OF MI-14 LCW & FLUORINERT LINES